SH-300 User’s Manual

                 Contents
SH-300 Text Panel
SH-300 User’s Manual                                          Hardware Part
               

Contents
1  3SH-300 Hardware part

1. 1  System General Introduction
3
1. 2  Specification Parameter
3
1. 3  Hardware Structure
4
1. 4  Function Key List
7
1. 5  Installation Dimensions and Guide
8
2  SH300 Software Part
11
2. 1  SH300 General Introduction
11
2. 2  Process Chart
11
2. 3  Installation and Uninstallation of SH-300
12
2.3.1 Installation of SH-300
12
2.3.2 Uninstallation of SH-300
15
2. 4  Operation Interface
16
2.4.1  File
18
2.4.2  Edit
18
2.4.3  View
19
2.4.4  Screen
20
2.4.5  Object
21
2.4.6  Connect
22
2.4.7  Tool
22
2.4.8  Help
23
2. 5  Operation Instruction
24
2.5.1  Indicator
24
2.5.2  Function Key
25
2.5.3  Static text
26
2.5.4  Dynamic text
27
2.5.5  Register
28
2.5.6  Bar Graph
31
2.5.7  Trend Graph
32
2.5.8  Bitmap
33
2.5.9  Message Display
34
2.5.10 Alarm List
35
2.6  User-defined SH300 system information
37
2.7  Multi Language Editor
47
2.8  Operation Example
49
3  Manipulation
56
3. 1  Download Window
56
3. 2  Communication
56
3. 3  Shifting the windows
57
3. 4  System Password
57
3. 5  Data setting
58
3. 6  State Monitoring
59
4  Connection with PLC
61
4. 1  Mitsubishi FX Series
61
4. 2  Siemens S7-200 Series
62
4. 3  OMRON C Series
63
4. 4  Delta DVP Series
64
4. 5  Panasonic FP Series
65
4. 6  Vigor VH Series
66
4. 7  Koyo S Series
67
4. 8  ADC DL05 Series
68
4. 9   FATEK FBs Series
70
4.10  Schneider NEZA/TWIDO Series
71
4.11  AB (AB-DF1 Protocol) Series
72
4.12  THINGET XC Series
73
4.13  Emerson EC20 Series
74
4.14  KDN-K3  Series
75
4.15  HITACHI MICRO-EH Series
76
4.16  MODBUS RTU/ASCII and RTU/ASCII EXTEND protocol
77
4.17  SH-300 Freedom Protocol
82
4.18  Array FAB Series PLC
90
4.19  Array SR Series PLC
93
4.20  Array TC-Pro Series Digital Timer/Counter/Tachometer
95
Appendix : Note item
97


SH-300 Hardware part                      1
1.1 System General Introduction
SH-300 is a small Human-Machine interface, mainly being used to be connected with PLC or other intelligent controllers with COM port communication function. It can monitor, setup and modify the data of the register or the status of the relay inside the PLC; thereby manipulators can monitor conveniently the PLC or the running status of the intelligent controllers with COM port communication function.

[Function features]
▲
The project development software SH300, built on WINDOWS platform, with friendly operation interface, easy to learn, being able to edit several monitoring screens and support multi-format graph.
▲
The communication protocols will be downloaded into SH-300 Text Display together with the project files. And it is unnecessary to edit the communication program in PLC separately. 
▲
SH-300 can be connected with many PLC. it supports Mitsubishi, Omron, Siemens, Panasonic ,Delta , Koyo ,Vigor ,ADC Schneider, AB PLC series and so on. it contains Modbus and freedom communication protocol 
▲
With password protecting function
▲
With alarm list function, real-time displaying the alarm information line by line.
▲

Having 14 keys, which can be defined as function keys, being easily operated, replacing 
some mechanical keys on the control cabinet, with the number key function.

▲
Supporting several kinds’ communication ports: RS232/RS422/RS485

▲
STN-LCD with back light display, displaying 24 characters X 4 rows

▲
With multi-language displaying function, with user-defined system prompting information, being convenient for different demands.

▲
The front panel being up to IP65 Protection Level, waterproof, oil proof
1.2 Specification Parameter
 —Hardware specification
	Display screen
	4.3’’STN LCD

	Resolution
	192 x 64 pixel

	LCM life
	With 25±2℃，65±10% RH over 50000 hours

	Brightness
	60 cd/m2

	Color
	Monochrome(yellow-green)

	Contrast
	Adjustable resistor

	Background light
	Long life yellow-green LED

	Memory
	110KB Flash ROM

	Communication Port
	PC RS232& PLC RS485/422 & PLC RS232

	Function button
	14 freely configurable keys 

	Allowable power disruption
	≤20ms

	Frame Dimension
	171.8 x 84.2 x 38.6mm

	Display Dimension
	97.0 x 34.5mm

	Installation hole

Dimension
	165 x 85mm

	Cooling Method
	Natural air cooling

	Weight
	260g


—Electric specification

	Rated voltage
	12 ~24VDC±10% <300mA 

	Withstanding voltage test
	500V AC 1minute(between signal and GND)

	Insulation resistance
	Over 10M ohm @ DC500V（between signal and GND）


—Ambient Requirement

	Operation ambient temperature
	–10℃~60℃

	Operation ambient moisture
	20~90%（no condensation）

	Storage temperature
	–20℃~70℃

	Anti-jamming test
	Voltage 1500Vp-p,pulse period 1us，continuing 1s

	Vibration resistance
	10~25Hz(2G for 30 min, in any of X,Y,Z axis)

	Degree of protection 
	IP65（the front panel） 


[image: image223.png]


[image: image224.png]


 

Caution!

Pay attention to the two polars of the power and the rated allowable voltage range, otherwise the main machine will be damaged.
[image: image225.png]



1.3 Hardware Structure

The front panel of SH-300 is as shown in the following figure. There is the 4.3’’STN LCD display at the top left corner. At the top right corner and the bottom there are 20 thin-film switch keys, which have a good handle and a long life. The Up Key, Down Key, ESC key, SET key, ALM key and ENT key are system keys. Except the basic function, the other fourteen keys can be set as special function keys to realize the Screen-jumping and digital setup functions. 

The front of panel of SH-300 programmable text display is shown as follows:
[image: image226.png]


[image: image227.png]


[image: image228.emf] 

T he picture for  8 pin Round shape    Female plug  

[image: image229.png]


      [image: image1.png]ARR/AY SH-300





Basic function of keys: setting the input value of the PLC registers.
Special function of keys: Bit setting, Bit resetting and Screen jumping etc.
On the right side of SH-300 there are power terminal and COM port and on the left side there is a contrast potentiometer. Refer to the following figure for details.
[image: image2.png]


                            [image: image3.png]



（Right side of SH-300）                     （Left side of SH-300）
When programming with SH300 software, please select the proper connection mode according to the type of PLC. After completing the edition, connect the SH-300 and the relative serial COM port of the PC via the programming cable SH-Cable. Then power on SH-300 and click the download icon to download the project file into SH-300.
When using if the contrast of the LCD isn’t fit, revolve the contrast potentiometer on the left side with small sized screwdriver till the contract reach the desired degree
The display of SH-300 is with LED background light. Press any key, the background light will be turned on automatically. The backlight will be turned off automatically if there is no operation in the minutes .Users can modify the turnoff time of the background light in SH300 software and then download into SH-300. And it will be OK.

The structure figure of SH-300 COM Port :
COM Port                   DC24V 
[image: image4.png](0102030405
L06070809 /





9 PIN male plug          power supply terminal
Pin Definition of SH-300 COM Port ：   
	Pin
	Definition

	1
	TD+

	2
	RXD

	3
	TXD

	4
	NC

	5
	GND

	6
	TD-

	7
	RTS

	8
	RD-

	9
	RD+


SH-Cable Wiring figure:
SH-300（9 PIN female plug）      PC（9 PIN female plug）

	RXD
	2

	TXD
	3

	RTS
	7

	GND
	5

	2
	RXD

	3
	TXD

	7
	RTS

	5
	GND


1.4 Function Key List
	key
	Function

	[←]
	When modifying the register data, the cursor will be moved one-digit left.

	[→]
	When modifying the register data, the cursor will be moved one-digit right.

	[↑]
	To jump to the previous screen, whose number is set in the screen property option. (The default value is the current number 1.)

In data-setting mode, pressing it, the modified number will be plus 1. The incremental range is 0 to 9 (in decimal system) and 0 to F (in hexadecimal system).

	[↓]
	To jump to the next screen, whose number is set in the screen property option. (The default value is the current number plus 1.)
In data-setting mode, pressing it, the modified number will be minus 1. The incremental range is 9 to 0 (in decimal system) and F to 0 (in hexadecimal system).

	[ +/- ]
	In data-setting mode, sign of the modified number will be set.

	[0-9 ]
	In data-setting mode, the modified number will be set as the corresponding number.

	[ESC]
	Exit from the current operation such as register set, password input, alarm display and so on.

	[ALM]
	Pressing this key, you can enter the system-defined alarm information screen. 

	[SET]
	Pressing this key, you can modify the register data. The current modified register will be color-reversely displayed and the current modified digital will be flashing. If there is no register set component in current screen, the operation is the non-operation. If press SET key again before pressing ENT, the current operation will be canceled and you can continue to modify the next register data

	[ENT]
	In the situation that the password protected function is used, pressing this key, the password set screen will be displayed.
In register-setting mode, pressing this key the modified data will be written into the register and then it will continue to modify the next register data.

When the last register in this screen is modified, pressing this key, it will exit the register modification state.

	[CLR]
	In data-setting mode, clear the set data.


1.5 Installation Dimensions and Guide                                                                                                                                                                  
Dimensions of SH-300 (L*W*H): 171.8×98.8×38.6 (Unit: mm)
Dimensions of the installation hole: 165×85 (Unit: mm)
[image: image5.png]AT IR

7%

85mm

AANNN N NN

-« >
165mm





Method 1： Embedded installation
The installment surface must be up to Standard Type 4, being applicable for indoor or the 
switchboard box on coequal condition.
Thickness of Clapboard: 0.5-0.9 mm.Dimensions of the installation holes are shown as follows:
[image: image6.png]00 '¥8

165.00




 [image: image7.png]



[image: image8.png]


     [image: image9.png]



Method 2：DIN rail installation（standard 35mm DIN rail installation）
[image: image10.png]@





Method 3: Screw installation (To install on the motherboard)
[image: image11.png]%16

{CD

aa
aa

ga
ga
aa
ga
ao
aao





[image: image12.png]1% 16

70. 00






SH300 Software Part                     2
2.1 SH300 General Introduction
SH300 is the special development software of SH-300 Programmable Text Display, which is run on the base of WINDOWS 98/2000/XP platform. SH300 software makes the best use of the abundant graphic interface and the object-faced design of WINDOWS, which makes it convenient for the users edit the required control screens and the alarm interfaces in a short time.
The essential of the project file is the Screen. Each screen is to perform some special functions and different screens can be switched freely via design. The aggregate composed of all the screens is the application project file.
After open the SH300 software, the user can create or open the screen. And in each screen static text, dynamic text, indicator, register, function key, bit graph, bar graph, trend graph and so on elements can be set. Different screens can be switched freely. Users can realize the data monitor, parameter setup, switch control, alarm list monitor and so on functions by designing the contents of the screen.2. 2 Process chart of using
2.2 Process Chart
The basic process chart of using is shown in the following figure:

[image: image13]
2.3 Installation and Uninstallation of SH300
2.3.1 Installation of SH300
The installation of SH300 is very simple. In the installation process, a prompting dialogue box will     appear automatically and you will complete the installation smoothly on the computer under its guidance. The main steps are as follows:
1. Insert the SH300 software CD into the CD Driver. Select the installation program file Setup.exe and click it , the following diagram will be shown:
[image: image14.png]SH300

up program. This progiam

vour compuer,

indows program

any proga
with th

i istibuton of this progiam, o any
il and and





▲ Click NEXT to enter the next installation step. The License Agreement will be shown as in the following diagram:
▲Click Cancel to exit the installation program.
[image: image15.png]£ 51300 Setup

SH300

ad the following
the rest of the agreement.





2. If you agree the above license agreement, please click YES to enter the next step. The interface requiring User Name, Company Name and Serial Number will be shown as follows:
[image: image16.png]SH300

[User Information





3. Fulfill the interface with the correct information and click NEXT to enter the installation path setting interface as follows:
[image: image17.png]SH300

etup il nsal i the follwing folder.

Tainstaltothis foder, lick N





▲ Click NEXT, the SH300 software will be installed in the default path as shown. If it is necessary  to select the path, click BROWSE to reset the desired path.
▲Click Back, it will return to the previous interface.
▲Click Cancel, it will exit the installation program.
4. Select NEXT to enter the next installation window;
▲ If Typical option is selected, all application components of SH300 will be installed;
▲ If Compact option is selected, the simplified components of SH300 will be installed;
▲ If Custom option is selected, user will be allowed to select the components of SH300.
[image: image18.png]SH300

[Setup Type

Clck the e

vou want o nstal.





[image: image19.png]


 Note: Selection of Typical option is recommended.
5. Select NEXT to enter the program aggregate displaying window as in the following diagram:
[image: image20.png]SH300

[Select Program Folder





▲ Click Next to start the installation program;
▲ Click Back to return to the previous interface;
▲ Click Cancel to terminate the installation program.
6. The installation program proceeds to the automatic installation procedure. Click Cancel, if you want to terminate now.
[image: image21.png]SH300





7. When the automatic installation process is completed, the setup finish window appears. Click Finish to complete the installation process. 
[image: image22.png]SH300

[Setup Complete

p s firished nstaling





2.3.2 Uninstallation of SH300
There are two ways for the uninstallation of SH300:
1. Remove from WINDOWS START MENU
▲ Under the WINDOWS taskbar, click Start→Program→ARRAY→SH300→Unistall of SH300  As shown in the following diagram:

[image: image23.png]Super CAD

i

FLER

|t uninstall sHaoo.

EL)/) 7] /) /6] 75 5] & »8 /T3] 75 ¢T5) 751 /5]





▲ When a confirm uninstall dialogue box appearing, click Yes and the following remove interface will appear.
[image: image24.png][Remove Programs From Your Computer.

uninstalShield will remave the software 'SH300 fiom your
computer, Please wat whie each of the folowing
components s reroved.
v Shared progiam fs.
v Standerd progiam fes.
v Folder tems.
Frogram folders

Frogram diectores.

Program sty enes

T

0%





2. Remove from the Console:
▲ Under the WINDOWS interface, double click My Computer and the management files of My Computer will be open.

▲ Double click and open the Control Panel. In the Control Panel, select Add/Remove Program icon and the Add/Remove Program dialogue box appears.
▲ After selecting the SH300 program folder in the said dialogue box, click Modify/Delete button and a dialogue box appears to ask if you want to remove the program. Click Yes and the remove interface will appear as the above diagram.

2.4 Operation Interface
The window of SH300 software is mainly made up of menu bar, tool bar, distribution bar, edit section, window description section, status bar and property section.
[image: image25.png]=101]

FielF) Ede(E) View(s) Srsen(s) Object(0) Comest(C) TookT) Hela)
O%EE S O A XAE Ty
?

Scre..| Description | | Scresn Edior

1

Property{Screen]
Sereen NO.

. e

Sereen Desciption

e —

‘When Up Artow key pressed, jump to screen NO.

i =]

When Down Artow key pressed, jump to scrzen NO.

EE

Mitsubihi(Fy) 7,31 Block{0/3] ENGLISH




	Tool bar
	[image: image26.jpg]H: 22X d0%edf s | 0BDA ARSIy S|






	[image: image27.bmp]
	Create a new project file

	[image: image28.bmp]
	Open a saved project file

	[image: image29.png]



	Close the current project file

	[image: image30.png]



	Save the current project file

	[image: image31.bmp]
	Cut components

	[image: image32.bmp]
	Copy components

	[image: image33.bmp]
	Paste components

	[image: image34.png]



	Delete components

	[image: image35.png]



	Create a new screen

	[image: image36.png]



	Delete the current screen

	[image: image37.png]



	Copy the current screen

	[image: image38.png]



	Set relative parameter of SH-300 Text Display

	[image: image39.png]



	Login in alarm list information, each piece of alarm information correspond to a status of a middle relay

	[image: image40.png]e




	Download the project into SH-300 via communication cable

	[image: image41.png]



	Indicator: displaying on/off status of PLC inner middle relay

	[image: image42.png]



	Function key: 14 keys on SH-300 panel being able to be defined as function keys, whose functions are screen-jumping and switch control etc.

	[image: image43.png]



	Static text, including Chinese characters, English characters and characters from other operation system

	[image: image44.png]



	Dynamic text, text content being able to be changed by PLC’s register.

	[image: image45.png]



	Register, placing the data-setting and data-setting components
(The operated object is the data register in PLC.)

	[image: image46.png]



	Bar graph, which can be used to monitor data change in PLC

	[image: image47.png]



	Trend graph, which can be used to monitor data change in PLC

	[image: image48.png]



	Insert the monochrome graphics file (Max. 192×64 pixels )

	[image: image49.jpg]



	Message display, which can display the status of PLC inner relay user-definedly.


	Distribution bar
	[image: image50.png]




	[image: image51.png]



	Place on the above layer

	[image: image52.png]



	Place on the next layer

	[image: image53.png][E=




	Left align all selected objects 

	[image: image54.png]B




	Right align all selected objects

	[image: image55.png]



	Up align all selected objects 

	[image: image56.png]



	Down align all selected objects 

	[image: image57.png]



	Left frame align all selected objects 

	[image: image58.png]



	Right frame align all selected objects 

	[image: image59.png][&




	Up frame align all selected objects 

	[image: image60.png]29




	Down frame align all selected objects 

	[image: image61.png]



	Align in the middle horizon all selected objects

	[image: image62.png]



	Align in the middle vertical all selected objects

	[image: image63.png]



	Align in the horizontal equal interval all selected objects

	[image: image64.png]



	Align in the vertical equal interval all selected objects


2.4.1 File

This instruction is mainly used for project file management, including creating, opening, saving etc
[image: image65.png]Fle(F) EdK(E) View(¥) Screen(s) Object(0) Comnect(C) Tool(T) Help(H)

0% gd= | en
?

D ew project(t) Ctrke
B Open profect(0)...  Ctr+O
W saveproject(s)  cies
Save Project As(a).

Close project(<)





	Menu Name
	Function

	New project
	Create a new project file

	Open project
	Open an old project file

	Save project
	Save the current project file

	Save as 
	Save the current file to a new path

	Close project
	Close the current project file

	Exit
	Exit SH300 software


2.4.2 Edit
This instruction is mainly used for tool management, including cut, copy, paste, delete, select all, control, position and so on. The pulldown menu is shown as the following:
[image: image66.png]Fie(F) | EdR(E) Viewly) Sereen(s) Objct(0) Comnect() ToolT) HeblH)
| O g et v @0 e gdls [en
I 3 B2 Copy(c) atie foole b i e 2 @

Paste(F) i)
Scrg X Delete(D) Dl

1 Select o it

2 e

en Edita

Al L)
Al riehtR)
Al tonT)

— Bk Al bottom(s)

Save Screen Bitmap
show back dot(G)

B Al sereen 0)
52 i sereen i e)
P 75l s topl)
g b Al screen bottom(D)

A g screen midE i) )
§ [ g screen iddEH)Y)

Iz o)

.2, Equel align(tH() creen NO.
PRSI —





	Menu Name
	Function

	Cut
	Cut components

	Copy
	Copy components

	Paste
	Paste components

	Delete
	Delete components

	Select All
	Select all components

	Control
	Change the arrangement

	Position
	Set alignment type

	Save Screen Bitmap
	Save the current screen as graph format

	Show Back Dot (G)
	Display 


2.4.3 View
This instruction is to display the toolbar, distribution bar and the status bar. The pulldown menu is shown as the following: 
[image: image67.png]e(F) EGi(E) | View(y) Screen(s) Object(0) Connect(C) ToolT) Help(H)

0% gd= | en
?

03 s |[v Tookar
+ Paistionbar

V sestusber
Scre... | Déscription
1

en Editor




▲ Toolbar: Toolbar displaying instruction
▲ Positionbar: Distribution bar displaying instruction
▲ Statusbar: Status bar displaying instruction
2.4.4 Screen
This instruction mainly includes new screen, delete screen, copy screen, set screen No., SH300 config and alarm list.
[image: image68.png]Fie(F) Edt(E) View(y) | Screen(s) Object(0) Comnect(c) TooT) Help(H)

0@ e @5 G newsaeent Bl @0
(2 Delete Screent(D). ?
& Copy creenC).

Scre
1

Descripti

& set screen NO(R).

57" 51300 Confin(s)
B alarm lis(L)




	Menu Name
	Function

	New screen
	Create a new screen

	Delete screen
	Delete the current screen

	Copy screen
	Copy the current screen

	Set screen No.
	Reset the screen number

	SH300 Config
	Set relative parameter of SH-300

	Alarm list
	Login the alarm list information; each piece of the information corresponds to a status of a middle relay


The “SH300 Config(S)…” option is used to set relative parameter of SH-300, such as set the boot screen number (the default screen number is 1.), password protection (the password will be number from 0 to 99999.) and screen save.
Screen Save
The duration time of the background light can be set freely.

When “Never” is selected, the background light will be on all the time;

When “After 3 minute ” is selected, the background light will be off 3 minutes later, if there is no operation on the key.

Notes: Pressing on any key will wake up the screen background light.
[image: image69.png]it sereen NO[ T 2 [o~zss]
Passward 0 2] [0~999309]

[-screen savers

screen savers [Afier 3 minute -

& Back Light Off

ok X carcel |





 

Caution!

The maximal number of the screen is 256.

2.4.5 Object
The instruction mainly includes Lamp, Touch Key, Static Text, Dynamic Text, Numeric, Process Bar, Trend Line, Picture and Message Display.
[image: image70.jpg]Sh300- watitledl.lsh

File(®) Edit(E) View®) Sercen(s) Comnect ) Toc

= [t e X|@ ®Lmn

31 Touch batton ()

[Scre...| Description | s.:veenE‘ASH
1

K Dymanic text

text

ZE Nuneric

D Bar Graph(s)
12 Trend Line @

W Pictwre®
£ Message Displey





	Menu  Name
	Function

	Lamp
	Displaying on/off status of PLC inner middle relay

	Touch button
	14 keys defined as function keys, which being used to realize the screen-jumping, switch control and so on functions.

	Static text
	Including Chinese characters, English characters and characters from other system

	Dynamic text
	Text contents can be controlled and changed by PLC register

	Numeric
	Register, placing the data-setting and data-setting components
(The operated object is the data register in PLC.)

	Progress Bar
	Bar graph, which can be used to monitor data change in PLC

	Trend Line
	Trend graph, which can be used to monitor data change in PLC

	Picture
	Insert the monochrome graphics file (Max. 192×64 pixels )

	Message Display
	Displays the status of PLC inner relay user-definedly.


2.4.6 Connect
The instruction is mainly used to Set PLC type, Set Communication Port and Download Data.
[image: image71.png]File(F) Edit(E) Wiew(¥) Screen(S) Object{O) | Connect(C) Tool(T) Help(H)
DEel OO setoktre)

Comm setings(C).

Sereen Editor B2 Download(D)

Scre... | Description




▲ Set PLC type: setting the linked PLC type and parameter
▲Comm Setting: selecting the communication port
▲ Download: download the project data file into SH-300
2.4.7 Tool
The instruction is mainly used for password protection and user-defined information including protect file password and immanent resource
               [image: image72.png]e(F) EGL(E) View(y) Screen(s) Object(O) Conmect(C) | TookT) Help(H)

D& d g% &

Protect fe password
Inmanent resource.

Sereen Editor

Scre... | Description
1





▲ Protect File Password: Set the SH300 project file to be password protected. 
[image: image73.png]Protect file password:

assword
T~ Set passwaord for open the

Password
Confirm

S| el |





▲ User-defined Immanent resource: to re-define the relative information of each interface in SH-300.

[image: image74.png]= message
o response
Passward menu
Input Passiord
Loginok

Passward erar
Logou ok

No alarm information

I~ User men seting

Hint

o]





2.4.8 Help
The menu mainly includes SH300 software version No. and other information.
[image: image75.png]Fie(F) EdiE) View(y) Screen(s) Object(0) Comect(Q) ToolT) | Hel(H)
DS H 0% &&= CEEE) ':
?

Sereen Editor

Scre... | Description
1





2.5 Operation Instruction (Mitsubishi FX Series as an example)

2.5.1 Indicator

Click “Lamp” option under “Object” menu or click [image: image76.png]


 in toolbar, there will be a dashed rectangular frame following and moving together with the mouse. Move the mouse to the proper position in the edit section and then click the left button of the mouse to confirm, and there will be one indicator in the edit section.
[image: image77.png]Screen Editor

Property [Lamp]
Posiion

x [60 =
v [z =
Style

I™ Dauble

Data setting
PLC Address

£l
Address

[o &

Type

|

Display
shape

Round ~]

Logic

Positve ~)




▲ Position Property:
   X Position: specifying the horizontal position of the component

   Y Position: specifying the vertical position of the component
Note: The grid origin is at the top left corner of the screen.

▲ Data Setting:

The number, type and address correspond to the definition of PLC inner relay.

▲ Style: Double: 

The displaying picture of the indicator will be double.

▲ Display:   
There are two shapes of the indicator: round and square.
There are two modes of the logic: positive and negative

	Logic Choice
	State
	Displaying Picture

	Positive Logic
	1
	[image: image78.png]




	Positive Logic
	0
	[image: image79.png]




	Negative Logic
	1
	[image: image80.png]




	Negative Logic
	0
	[image: image81.png]





In positive logic, if the corresponding middle relay is ON, the indicator will be solid; and if the corresponding middle relay is OFF, the indicator will be hollow.
In negative logic, if the corresponding middle relay is ON, the indicator will be hollow; and if the corresponding middle relay is OFF, the indicator will be solid.
2.5.2 Function Key

Click “Function Key” option under “Object” menu, or click [image: image82.png]


 in toolbar, there will be a dashed rectangular frame following and moving together with the mouse. Move the mouse to the proper position in the edit section and then click the left button of the mouse to confirm, and there will be one indicator in the edit section. 
[image: image83.png]Screen Editor

Praperty [Touch button]

Posiion

x [z

¥ 12 [
Style
I™ Double

I™ Reverse

“Touch button
Key

[ |

I™ Hand
I Invisble

I™ password

Action
© set col

€ Jump to

€ Set Register

set Col
PLC Address
Address

0o IE

& oN
 oFF

Tye

T

C Reverse



 
▲ Position Property:
   X Position: specifying the horizontal position of the component

   Y Position: specifying the vertical position of the component
Note: The grid origin is at the top left corner of the screen.

▲ Function key Property
   Key: to select any proper key from Left .Right.+/-.CLR. 0-9 14 keys 
   Hand: to add a hand shape symbol before the selected key, which indicates that pressing the key will carry out an operation for the convenience of use.

   Invisible: to hide the key

   Password: The function key will be effective, only when the password is entered
correctly.
   Coil Set: Action of the function key is defined as digit setup function.
   Screen-Jumping: Action of the key is defined as screen-jumping function.

   Register Set: Action of the key is defined as register parameter setup function.
▲Coil

   The number, type and address correspond to the definition of PLC inner relay.

   ON: to set the designated relay to be ON.
 OFF: to set the designated relay to be OFF.
Reverse: Press this key, the value of the designated relay will be reversed.
▲ Style 

   Double: The displaying picture of the indicator will be double.

   Reverse: The function and the background color will be reversely displayed.
2.5.3 Static text

Click “Static Text” option once with left button of mouse of menu “Object”, or click [image: image84.png]


 once in toolbar, there will be a dashed rectangular frame following and moving together with the mouse. Move the mouse to the proper position in the edit section and then click once the left button of the mouse to confirm, and there will be one indicator in the edit section.
[image: image85.png]Screen Editor

Property [Text]

Pasiion it Strng
e

v [ roct
Style

™ Double

I™ Reverse




▲ Position Property:
   X Position: specifying the horizontal position of the component

   Y Position: specifying the vertical position of the component
Note: The grid origin is at the top left corner of the screen.

▲ Input String:
   To input relevant text explanation, which can be input 24 English characters*4 rows or 12 Chinese characters*4 rows

▲ Style 

   Double: The static textbox will be double relatively.

   Reverse: The static textbox and the background color will be reversely displayed.
2.5.4 Dynamic text

Click “Dynamic Text” option under “Object” menu, or click [image: image86.png]


 in toolbar, there will be a dashed rectangular frame following and moving together with the mouse. Move the mouse to the proper position in the edit section and then click the left button of the mouse to confirm, and there will be one indicator in the edit section.

[image: image87.png]Screen Editor

Property [Dynamic Text]

Position Data setting
PLC Address Type
X |44 2 dpb =
Y [i5 2]| Addess
o 2
Style Data type
oot | HEXECD
 DEC
I~ Reverse

I signed

Display text
[Vaue [Cantent
1 Dynamic Text





▲ Position Property:
   X Position: specifying the horizontal position of the component

   Y Position: specifying the vertical position of the component
Note: The grid origin is at the top left corner of the screen.

▲ Style 

   Double: The static textbox will be double relatively.

   Reverse: The static textbox and the background color will be reversely displayed.
▲ Register

   To control the address and the type of the PLC register that switches the dynamic text state. The “Data Type” is the corresponding PLC register type connected to the PLC. The “Address” is the corresponding PLC address connected to the PLC. The “Mode” has 3 options, HEX/BCD, Decimal system and symbol, which is to control the data format of the data register and will influence the displaying format of the value in the displaying text.
▲ Display Text

Text edit zone, to input the displaying text (up to 32 rows text)
Example: The register address of the related dynamic text is D100. In the first line, input “motor speed is too rapid” and modify the value to 80. In the second line, input “motor speed is too slow” and modify the value to 40. And in the third line, input “motor speed is normal” and modify the value to 60. The dynamic text responds to the data of 

   D100. 

If the value of D100 is the unset value, then the textbox will be no displaying.

If the value of D100 is 40, the “motor speed is too slow” will be displayed as follows:
[image: image88.png]motor speed is too slow





If the value of D100 is 60, the “motor speed is normal” will be displayed as follows:

[image: image89.png]



If the value of D100 is 80, the “motor speed is too rapid” will be displayed as follows:
[image: image90.png]



2.5.5 Register

Click “Register” option under “Object” menu, or click [image: image91.png]


 in toolbar, there will be a dashed rectangular frame following and moving together with the mouse. Move the mouse to the proper position in the edit section and then click the left button of the mouse to confirm, and there will be one indicator in the edit section.
[image: image92.png]Screen Editor

Property [ Numeric |

Postion Format Data setting
« prTa | 2ot PLC Adess Max input
=I5 73] z T set ==
Y [ 2 || Decmal Type = Min input
oIz p =l I Limite. TE]
style Data type Address o =] Eng: Max
Crexpo o (3] ==
I~ Double

QbE Registers Eng. min

I~ Reverse I™ Signed L[ =




▲ Position Property:
   X Position: specifying the horizontal position of the component

   Y Position: specifying the vertical position of the component
Note: The grid origin is at the top left corner of the screen.

▲ Style 

  Double: The register will be double relatively.

Reverse: The register and the background color will be reversely displayed.
▲ Format

  Set the digits, decimal digits and the display mode of the register data. The display mode has 3 options, HEX/BCD, Decimal system and symbol.
▲ Register

  To set the type and address of the related PLC register. The “Type” is the corresponding PLC register type connected to the PLC. The “Address” is the corresponding PLC address connected to the PLC. The “Mode” has 3 options, HEX/BCD, Decimal system and symbol, which is to control the data format of the data register and will influence the displaying format of the value in the displaying text.

SET

If cross the “Set” check box, the “Password” option will be displayed. When the “Password” option is selected, if user wants to set the value via “SET” key on the SH-300 panel, it is needed to press “ENT” key to enter the password interface and input the correct password.

Limit

To set the upper and lower limit, make the value beyond the limit invalid and avoid the input of too large or too tiny value to endanger the system.

    Example: If the set upper limit is 800, and the set lower limit is 100. Only when the set value is between 100 and 800, the set value will be written into the PLC. Otherwise it will wait to set the new valid value.

    After “Limit” is selected, users can select “Original Data” or “Engineering Limits”. 

Original data:

Original Data means the directly displaying register value without any operation. And the radix point will be placed according to the decimal digits. If the decimal digits are 2 and the register value is 24561, the displayed data will be 245.61.
Engineering Limits

The maximum and minimum of the project data
Project data

This option means that the data read from the register will be converted to project data before being displayed. The conversion is done following the formula below:

The converted data=project Min + (original value- input Min) × (project Max- project Min) / (input Max-input Min) 
Example: the data value stored in the register is 1000, do the setting as follows:

Max Input: 4000
Min Input: 0

Max Project: 2000

Min Project: -2000

Then by conversion the project data =-2000 +（1000-0）× (2000+2000)/(4000-0)= -1000
 

Caution!

There may be some error in the conversion because of the limit of the operation precision of the floating number. 


For example: Design requirements: Screen 2 is two groups of the main property parameter of the related PLC, the rotate speed of principal axis and the rotate speed of the countershaft. The left column is the set value and the right column is the actual value. And the corresponding relationship of the two groups of parameters and the PLC data register address is as the following table:
	Designation
	Address for preset value
	Address for actual value

	Primary Axis Speed
	D100
	D110

	Secondary Axis Speed
	D200
	D210


The procedure of creating Screen 2 is as below:

Create Screen 2. Then set “Target”, ”Current”, ”Primary”, ”Secondary” in the proper position in the screen as shown in the following:

[image: image93.png]"""" Target Current





Select “Register” option or click [image: image94.png]


 in the tool bar; move the mouse to the proper position under “Target” and click the left key of the mouse to confirm. Do the settings as below: register address=D100, register number=1, digits=5, decimal=0, mode=Dec, the negative number will not be displayed.

Select “Set” check box, and “Password” options is enabled , “Password”  “Limit” can be set according to the demands. Set D200 as above data set method.
Select “Register” option or click [image: image95.png]


 in the tool bar; move the mouse to the proper position under “Target” and click the left key of the mouse to confirm. Do the settings as below: register address =D110, register number=1, digit=5, decimal=0, mode=Dec, the negative number will not be displayed. And don’t select “Set” check box. Set D210 as above method.
After all parameters are set, the following diagram will be shown:
[image: image96.png]......... Target Curran
Primary. | [123451 2345

Secondary 1234512345




2.5.6 Bar Graph

Click “Bar Graph” option under Object” menu,click [image: image97.png]


 in toolbar, there will be a dashed rectangular frame following and moving together with the mouse. Move the mouse to the proper position in the edit section and then click the left button of the mouse to confirm, and there will be one indicator in the edit section.
[image: image98.png]Screen Editor

Property[ Graph bar ]

Postion Data setting Display
X [re 4] | PLC Address Type T i
2] 65535 2
vEE A = ¢ rexeo
Low
< address & DEC
ize ~ g =
CE =
with]16 2 I~ signed Fil drection

Registers

hont [s2 2] [ 12 b~




▲ Position Property:
   X Position: specifying the horizontal position of the component

   Y Position: specifying the vertical position of the component
Note: The grid origin is at top left corner of the screen.

▲ Register

   Set the address, number, type and mode (HEX/BCD, Decimal system and symbol) of the related register.

▲ Size

   Set the height and width of the bar graph.
▲ Display

Full amount: 100% bar graph will display the corresponding register value

Empty amount: 0% bar graph will display the corresponding register value

   Direction: the direction of the bar graph includes four options: up, down, left and right.
Example: Create a bar graph about precipitation and the display range is 0-100mm. Put the texts “mm”, “precipitation”, “0”, “100” in proper position as shown in the following diagram: 

[image: image99.png]Screen Editor

Taalaal

Property{Screen]
Sereen NO.

C—

Sereen Desciption

e —

‘When Up Artow key pressed, jump to screen NO.
EE
When Down Artow key pressed, jump to scrzen NO.

5 =




This bar graph can be used to monitor the data in register D0. If the bar graph is fully displayed, it means the value in register D0 is 100. And when the bar graph is 20% displayed, it means the value in register D0 is 20.
2.5.7 Trend Graph
Click “Trend Graph” option once with left button of mouse of menu “Object”, or click [image: image100.png]


 once in toolbar, there will be a dashed rectangular frame following and moving together with the mouse. Move the mouse to the proper position in the edit section and then click once the left button of the mouse to confirm, and there will be one indicator in the edit section.
[image: image101.png]Screen Editor

Property [Trend Line |

Postton Data satting
x fig 2| pic addresype FDE:E;V;D
vF 3 AP e o

Acress ™ sgned
Size: o =

wdth [ T3] gt
rignt i 2] [T 12

Display
Hh

65535 =

Low
o =
Data sample
EE
Sample Interval

5 +| sec




▲ Position Property:
   X Position: specifying the horizontal position of the component

   Y Position: specifying the vertical position of the component
Note: The grid origin is at the top left corner of the screen.

▲ Register

   Set the address, number, type and mode (HEX/BCD, Decimal system and symbol) of the related register.

▲ Size

   Set the height and width of the trend graph.
▲ Display

Full amount: 100% trend line will display the corresponding register value

Empty amount: 0% trend line will display the corresponding register value

   Date dots: the total sample number in the whole trend line from left to right. The more the number is, the trend line will be more fine and the time will be longer.
Sample interval: the interval between two neighboring sample dots.
[image: image102.png]


 Note: A trend line component can only display one line.
2.5.8 Bitmap

Select “Bitmap” option under “Component” or click [image: image103.png]


 icon in the tool bar, the following prompting frame will be shown:
[image: image104.png]My Recent
Documents

@

e

&
iy

g

My Computer

My Network
Places

Lookin: [ &9 dswitcht = e B
S dsmechonta [ domechoosg 3 domechoosh
S dswechootb (N dowechoosh (4 cewechotoa
S dswechonza [ dowechonsa (4 dowechotoh
S dswiechonz (S dowechooeh [ dowechot1a
S dswechonze (S dowechonsc (5 dowechot b
S dswiechonsa (S dowechooed [ domecho1za
S dswiechonsh (N dowechonse [ dowech01zh
(SRt Cp—
(S C———
S dswiechosa (4 comechooh
S dswichonsh (4 comchooza
S dswechoose |
(S dswichoosd [~ dswechoos
‘mmhnnse S dswitchonst
‘aawmm S dsmechonsa
- [tchaczs &l Open
Files of type: Al files [*jpg:" ipeg:".bmp."ico] o Cancel





Select your desired picture and then click “Open” option. The selected picture will be put in the edit window, as shown in the following diagram:
[image: image105.png]Sereen Editor

Property| Piture |

Posiior:
x[E 3

v 3

Size

widh [z 3]
e

hight

e




▲ Position Property:
   X Position: specifying the horizontal position of the component

   Y Position: specifying the vertical position of the component
Note: The grid origin is at the top left corner of the screen.
▲ Size

   To adjust the height and width of the bitmap

▲ Reverse

     The color of the picture and the background will be reversely displayed.

 
Note: SH300 software can support many kinds of graphic files, such as *BMP, *ICO, *JPG etc.
2.5.9 Message Display
Select “Message display” option under “Component” or click [image: image106.jpg]


 icon in the tool bar, the following prompting frame will be shown. Click the left key of the mouse to confirm after moving the mouse cursor to the proper place of edited area.
[image: image107.jpg]Sereen Editor

Property [Lanp]

Position Data setting
PLE Address Type Adiress
x =
P A =k =
|
Strle Hessage:

Font L T

[ Reverse || OFE Massage: [OFF




▲ Position Property:
 X Position: specifying the horizontal position of the component

Y Position: specifying the vertical position of the component
Note: The grid origin is at the top left corner of the screen.
▲ Coil Property
   Station number, type and the address correspond to the type of PLC relay.
▲ Style
   Font: the type and size of displayed message are changeable.

   Reverse: the background color will be reversely displayed.

▲ Message
   On Message: the content is editable, and will be displayed when the coil is ON.
   Off Message: the content is editable, and will be displayed when the coil is OFF.
2.5.10 Alarm List

Select “Alarm List” option under “Window” or click [image: image108.png]


 in the tool bar, the following prompting frame will be shown:

[image: image109.png]Alarm Setting

" Data Setting
PLC Address Type  Address

F 3 kAP B

Index | col Alarm description

add Tnsert Delete ok " Cancel





Each project file of SH-300 can set a group of alarm list information. And each piece of information corresponds to a relay. The definition numbers of all the relays are continuous. And the first addresses of all the relays are set by the users according to the actual program. If any relay changing from OFF to ON means the relative alarm is produced, and now the SH-300 will prompt the alarm displaying screen automatically and the alarm information will be displayed in the first row. If another relay is ON now, the new piece of alarm information will be displayed in the second row. On the contrary, if any alarmed relay is OFF, the related alarm information will disappear automatically.

Example: Create a group of alarm information about pump. Set Relay M100, M101, M102 and the related alarm information contents are “over 5m for water level”, ”overload for pump”, ”error for power”.

The operation procedures are as the following:
1. Set the first coil type as M, the initial as 100.
2. Input “Water level is over 5m” in the line of the alarm contents bar. Click “Add” button or press “Enter” key to add the second line and input “Pump overload”. By the same method, add the third line and input “ Power supply fault”.
[image: image110.png]Alarm Setting

Data Setting

PLC Address Type

Address

Index | col Alarm description
o [water level s over sm
1 [pump overioad
[power supply fault
g
Add Insert Delete ok Cancel





When SH-300 is working normally, if there is any failure alarm or M0 and M2 are ON, the flashing alarm screen will prompt automatically on SH-300 as in the following:
[image: image111.png]weatar level is over G




If the alarm failure is not corrected, the failure alarm information will flash and be displayed on SH-300. If the failure is corrected, the SH-300 will resume normal display. If the system is in examination and repair, user can check the failure alarm records via the “ALM” key on the panel. After the checking, press “ESC” key to return to the main interface.
2.6 User-defined SH300 system information 
SH300 provides completely open system information menu structure, which provides user with completely self-defined menu. You can use any language system to edit your information menu and at the same time the coordinate position of the menu can be relatively changed according to your demand.

After standard installation of SH300 software, the default information menu will be loaded automatically when downloading data. The menu option lies in the submenu “Immanent resource” of the menu “Tool”.

[image: image112.png]5h300- untitlec

FelP) EGKE) Vw(s) Screens) Objecio) Comnedt(Q) | Toolh) Hebt)
EECIE TR R
e | Mocrrmtion | ~Screen Editor

Protect fe password





Click “Immanent resource“, then the following diagram will be shown:      
 [image: image113.png]Juse |
(oo
¥ Uset menu seing st | smve ose

Hint





Click “default” and then doubt click “message” on the left column. The seven information submenu “No response”, “Password menu”, “Input Password”, “Login OK”, “Password error”, “Logout OK”, “No alarm information” will be displayed as in the following diagram:

[image: image114.png]Hint





Click the “no response” submenu, the communication interface information between SH-300 and PLC will be displayed as in the following diagram:
[image: image115.png]= message

©
Passward menu

Input Passiord
Loginok

Passward erar
Logou ok

No alarm information

Hint

User menu selfing

M RES

o]





If the text and the position of the information in the screen need to be changed, cross “user menu setting” check box and doubt click “No response…”, the following prompting frame will be displayed as the following:
[image: image116.png]E——— "

~Postion———

o
! [T =]

v 2

[-Input Stin

NO RESPONSE

_ el | Ok Carcel





In this property frame, user can modify the X and Y coordinate position of the menu information (at the top left corner, it is the original coordinate position (0, 0) of X and Y) and the contents of the text information of the text frame (supporting multi language system). If “Default” is selected, which means the default interface will be displayed when communication. The displayed text is “no response…” and the coordinate position is X0 and Y0 as in the following diagram when SH-300 is communicating with PLC.
[image: image117.png]



Example: Modify the default text from “no response” into “transmit data” and preserve the coordinate position. Click “OK” button to confirm. After the modification, when SH-300 is communicating with PLC, the following diagram will be displayed. 
[image: image118.png]



Click the “password menu” submenu, the password set interface will be displayed as in the following diagram. The password is the same one as set under the submenu “SH-300 Config” of the menu “Screen”.
[image: image119.png]= message

No resporse
Password menul
Input Passiord
Loginok
Passward erar
Logou ok

. 1.LOGIN

7 Uset men seting

2, LOGOUT
EXIT

Hint
2]





The password set interface includes “LOGIN”, “LOGOUT”, “ESC EXIT” (default information).
If the text of the information in the screen need to be changed and the position need not to be changed, cross “user menu setting” check box and doubt click the text needed to be changed, the following prompting frame will be displayed as the following:

 [image: image120.png]xl
T ——— "

Posiion————|

==

[-Input Stin

defoult ok =





In the above property frame, the text information contents can be modified in the text frame (supporting multi language system). If “Default” is selected, the default password interface will be displayed. The displayed text is “LOGIN”, “LOGOUT”, “ EXIT”. In the password set situation, press “Enter” key, the following diagram will be displayed:

[image: image121.png]



Example: Substitute the text “ENTER” for “LOGIN”, “QUIT” for “LOGOUT” and “RETURN” for “EXIT”. Click “OK”, the following diagram will be displayed.
[image: image122.png]



Click the “Input password” submenu, then the password input interface will be displayed as in the following diagram.

[image: image123.png]= message
No response
Passward

Login ok

Passward erar
Logou ok
No alarm information

I~ User men seting

Hint

[TE]





If the text and the position of the information in the screen need to be changed, cross “user menu setting” check box and doubt click “Input Password”, the following prompting frame will be displayed as the following:

[image: image124.png]Proverty [Text] |

Propety Tetl |

~Postion——— o

# = 1005 =
v E -l

[-Input Stin

Input Password
et ok Carcel





In this property frame, user can modify the X coordinate position of the menu information and the Y coordinate position is fixed (at the top left corner, it is the original coordinate position (0, 0) of X and Y) and the contents of the text information of the text frame (supporting multi language system). If “Default” is selected, which means the default interface will be displayed when communication. The displayed text is “Input password” and the coordinate position is X40 and Y8. And the position of the password input is also fixed as in the following diagram:
[image: image125.png]CINPUT PASSWORD -





Example: substitute the text “password” for “Input password”, modify the position X to 0 and the position Y is fixed. Click “OK”, the following diagram will be displayed:
[image: image126.png]



Click the “Login OK” submenu, then the password being successfully input interface will be displayed as in the following diagram:

[image: image127.png]= message

No response
Passward menu
Input Passuerd

Password ror
Logout ok
No alarm information

7 Uset men seting

Hint

LeST

PRES

[0]





In this interface, there are two lines of texts “Login Success”, “Press any key” (default information).

If the text and the position of the information in the screen need to be changed, cross “user menu setting” check box and doubt click the modifying text(take “Login Success” for example) the following prompting frame will be displayed as the following:
[image: image128.png][

Posiion——— 0
x| = [ios 2|

v =

[“Input Stiing

LOGIN SUCCESS
defauit ok Cancel





In this property frame, user can modify the X and Y coordinate position of the menu information (at the top left corner, it is the original coordinate position (0, 0) of X and Y) and the contents of the text information of the text frame (supporting multi language system). If “Default” is selected, which means the default interface will be displayed when communication. The displayed text is “Login Success” and the coordinate position is X38 and Y8 as in the following diagram: 
[image: image129.png]- LOGIN SUCCESS - - -




Example: Substitute the text “CORRECT PASSWORD” for “LOGIN SUCCESS” and “CONTINUE” for “PRESS ANY KEY”. Then click “OK”. The following diagram will be displayed:
[image: image130.png]CORRECT FASSWORD





Click the “Password error” submenu, the password being error prompting interface will be displayed as in the following diagram:
[image: image131.png]s [x]

= message

Noresponse ¥ User menu seting defoult Save Close

Passward menu
Input Passiord
Login ok

Logout ok
No alarm information

WORD ERROR

FRE AMNY KEY

Hint

] =





In this interface, there are two lines of texts “Password Error”, “Press any key” (default information).

If the text and the position of the information in the screen need to be changed, cross “user menu setting” check box and doubt click the modifying text (take “PASSWORD ERROR” for example), the following prompting frame will be displayed as the following:
[image: image132.png][=i
EE———

~Postion———

_— P—
b = 1008

o El
e

PASSWORD ERROR

defoult ok ra—





In this property frame, user can modify the X and Y coordinate position of the menu information (at the top left corner, it is the original coordinate position (0, 0) of X and Y) and the contents of the text information of the text frame (supporting multi language system). If “Default” is selected, which means the default interface will be displayed when communication. The displayed texts are “PASSWORD ERROR” and “PRESS ANY KEY” as in the following diagram: 
[image: image133.png]- PASSWORD ERROR - -

- PRESS ANY KEY





Example: Substitute the text “PASSWORD ERROR” for “IT IS WRONG” and “CONTINUE” for “PRESS ANY KEY”. Then click “OK”. The following diagram will be displayed:
[image: image134.png]



Click the “Logout OK” submenu, the password being closed interface will be displayed as in the following diagram:

[image: image135.png]= message

No response
Passward menu

Input Passiord
Loginok

Passward erar

No alam information

7 Uset men seting

Hint

01E]





In this interface, there are two lines of texts “LOGOUT SUCCESS”, “PRESS ANY KEY” (default information).

If the text and the position of the information in the screen need to be changed, cross “user menu setting” check box and doubt click the modifying text (take “LOGOUT SUCCESS” for example), the following prompting frame will be displayed as the following:
[image: image136.png]Property [Text]

oo

Posiion————|

. —
) = 1010

| E
Tz

LOGOUT SUCCESS

defoult ok -





In this property frame, user can modify the X and Y coordinate position of the menu information (at the top left corner, it is the original coordinate position (0, 0) of X and Y) and the contents of the text information of the text frame (supporting multi language system). If “Default” is selected, which means the default interface will be displayed when communication. The displayed texts are “LOGOUT SUCCESS” and “PRESS ANY KEY” as in the following diagram: 

[image: image137.png]- LOGOUT SIUCCESS - -
. PRESS ANY KEY. - - -





Example: Substitute the text “REWRITE PASSWORD” for “LOGOUT SUCCESS” and “CONTINUE” for “PRESS ANY KEY”. Then click “OK”. The following diagram will be displayed:

[image: image138.png]REWRITE PASSWORL:

CCOMNTIMNUE -





Click the “No alarm information” submenu, there being no alarm in the program prompting interface will be displayed as in the following diagram:

[image: image139.png]= message
No response
Passward menu
Input Passiord
Loginok
Passward erar
Logout ok

7 Uset men seting

Hint

[g)





If the text and the position of the information in the screen need to be changed, cross “user menu setting” check box and double click the text frame “NO ALARM INFORMATION”, the following prompting frame will be displayed as the following:
[image: image140.png]~Postion———

5
E_3 —

No alarm information

defoult 0k Cancel




In this property frame, user can modify the X and Y coordinate position of the menu information (at the top left corner, it is the original coordinate position (0, 0) of X and Y) and the contents of the text information of the text frame (supporting multi language system). If “Default” is selected, which means the default interface will be displayed when communication. The displayed text is “NO ALARM INFORMATION” and the coordinate position is X16 and Y24 as in the following diagram: 
[image: image141.png]L MNe alarm |r‘|Format|om




Example: Substitute the text “alarm didn’t happen ” for “NO ALARM INFORMATION”. Then click “OK”. The following diagram will be displayed:

Under actual operation, if there is no alarm happens, press “ALM” key, the following diagram will also be displayed:
[image: image142.png]



Note: After the modification of the self-defined information menu, click “Save” button and close the information frame, and write the edited program into SH-300, then the modified self-defined information will be written into SH-300.

2.7 Multi Language Editor

SH300 provides completely open multi language menu structure, which provides user with completely self-defined menu. You can use Chinese, English, French, German Czech and any other language to edit your message menu.

LangEditor is a characteristic language editor, which makes it reality that the menu supported SH300 software will be displayed in multi language.

After installation, the default English system menu will be loaded automatically in SH300 software. Open the LangEditor.exe file in SH300 software installation folder, the following interface will be displayed.



       [image: image143.png]SH300 Language Editor =10lx|
Language Tool tHelp

MyEngish ii
SH300 software

Newfle

Dowload project
FieftF)

New profct(sH) L

New projeciCreate a new piect

Open project0).

Open projectiOpen an existing document

3 Save project(ts)

i Save projsctSave the document
i Save Froject AsitAl

2 Save Froject ast3ave the document with an new name.
13 Close project(sC)

i Close projectCloss the document

Eie)

EdEst

[-Engish
[New profect)

9]
Approve Changes|

[-Messa

||





※Default reference bar: to display the default English menu bar;

※Display Message Bar: to display the modifying message bar;

※Display Message: to display the message menu;
※Modification Message: to modify the message menu;
※Note Bar: in find function, the relative message after finding will be displayed in the bar.

Click “language” menu, the pulldown menu is shown as the following, including “Open Language File”, “Save language File’’, “Close Language File” and “Exit”.

     [image: image144.png](& Open Language File crlor
M 5eve Language File Cirlts
W Ciose Language File

IR Ext At

3 Dowload project

4 FieftF)

5 New projectsH)

6 New projectiCreate a new project





Take a text as an example to introduce the operation of the SH300 Langeditor.
Example: substitute the text “user-defined system information” for “Immanent resource”.
First, run the “Langeditor,exe” file . 

Second, click Language→Open Language File→English in the Language Menu. 

Then click “Search” under “Tool” menu.

The following diagram will be displayed.
[image: image145.png]Input Box

cachMessage |

[MessageType |

Search

Cancel

[New Message





Input the text “Immanent resource” in the Search Message text frame. Choose “Original” as Message type. Then click “Search”. The information you want to change will be displayed in the Remark Bar as in the following diagram:
[image: image146.png]114 Immanent resavrce.





From the search result, the searched “Immanent resource” lies in Line 113 and Line 114. Browse Line 113 and Line 114. Double click Line 113, and the “Immanent resource” will be changed into “User-defined system information” in the Modification Message bar. By the same method, do the modification in Line 114.
Then, click “Approve Change” to confirm the modification.

Finally, select Language → Save Language File or press Ctrl+S to save the file and then exit the language editor.

Reopen the SH300.exe file and the relative modified menu will be found modified.
2.8 Operation Example

Subject: The Drying Boxes Control System

Control requirements:

（1）Via SH-300 to monitor the work status of three groups of heating units;
（2）Via SH-300 to observe the actual temperature and change the preset temperature of the drying boxes;

（3）Via SH-300 to observe the actual speed and change the preset speed of the motor;

（4）Via SH-300 to set alarm information of abnormal work;
Operation Procedure:

1. Open SH300 software and click “New Project”, a prompting dialogue frame will be shown as follows:
Select PLC type (take Mitsubishi (FX) for example), COM port and the other corresponding parameter and then click OK to confirm.
[image: image147.png]| Newproject = k1)

~Target PLC/Ceontroller Type

pLC

~Communication port——|-Communication settings

Badrate o0 |
seralp[comi ] | Databits
stopgts 1 |

| partty EE——|

K X cancal |





2. Make the main Screen 1 “Drying Box Control Menu” and input the text “Drying Box Control Menu” in the screen description bar. 

Set function key ①, set its property for jumping to Screen 2 and input the text “Temp” for temperature setting on its right;

Set function key ②, set its property for jumping to Screen 3 and input the text “State” for state monitoring on its right;

Set function key ③ , set its property for jumping to Screen 4 and input the text “Motor” for motor setting on its right;

Input the text “【ALM】Alarm list” which can prompt user to press ALM key to enter alarm list bar.
[image: image148.png]DryingboxControlMenu:
@D Temnp @ State @Motor




3. Make Screen 2 “Temperature Setting”
Click “New Screen” or [image: image149.png]


 icon, the following dialogue frame will be displayed:
[image: image150.png]Sereen NO.
B

Sereen Description

e —

When Up Arrow key pressed, jump to screen NO

||

When Down Arow key pressed, Jump to screen

||
Ok Cancel





   Correctly select “2” as the screen number, input the screen description “Temperature Setting”,select “1” as the up-jumping screen number and select “3” as the down-jumping screen number as in the following diagram:
[image: image151.png]Sereen NO.
B

Sereen Description

[Temperature setting

When Up Arrow key pressed, jump to screen NO

||

When Down Arow key pressed, Jump to screen

||
Ok Cancel





Press “OK” key to confirm and enter Screen 2. And place the text “Target”, “Current”, “Temp” in proper place as the following diagram: 
[image: image152.png]



   Select “Register” under “Object” menu or click [image: image153.png]


 in the tool bar. Move the mouse to proper

place under “Target” and click the left key of the mouse to confirm. Then set the parameter of the register, Address=D0, Digits=4, Decimal=2, Mode=Dec. Select “Set” and “Limit” check box. Then place the text “℃” on its right as shown in the following diagram: 
[image: image154.png]‘Screen Editor

Property [ Numeric |

Postion Format Data setting
. B oot PLC Address M input
=l [ = W set T
v [ T3] | Decmal e I~ Password i input
= b =~ W Limite o z
Style Data type Addhess [origina =] Eng. Max
© HEX/BOD RS =
I” Double

QbE Registers Eng. min

I~ Reverse I™ Signed L[ =




Select “Register” under “Object” menu or click [image: image155.png]


 in the tool bar. Move the mouse to proper place under “Current” and click the left key of the mouse to confirm. Then set the parameter of the register, Address=D1, Digits=4, Decimal=2, Mode=Dec. Don’t select the “Set” check box. Then place the text “℃” on its right as shown in the following diagram: 
[image: image156.png]Screen Editor

Property [ Numeric ]

CEEEE T e s
v [0 4] | Decimal Type - Min input
13 o~ I~ Limite =]
Style Data type: Address [orignal =] Eng. Max
" HEX/BCD. S ==E
I” Double

& DEC Registers Eng. min

I Reverse || Sioned = 2




4. Make Screen 3 “State Monitoring”
As stated above, create the Screen 3. The input the text “Heating Unit 1”, “Heating Unit 2”, “Heating Unit 3” in proper place in the screen as in the following diagram: 
[image: image157.png]



Select “Indicator” under “Object” menu or click [image: image158.png]


 in the tool bar. Move the mouse to proper place behind “Heating Unit 1” and click the left key of the mouse to confirm as in the following diagram. And add two other indicators as the above. 
[image: image159.png]Heating Unit 1 °

Heating Unit 3¢





Set the “Indicator” one by one.

The setting of the indicator for the heating unit 1 is listed as below: Address=M30, Shape=Square, logic=positive;

The setting of the indicator for the heating unit 2 is listed as below: Address=M40, Shape=Square, logic=positive;

The setting of the indicator for the heating unit 3 is listed as below: Address=M50, Shape=Square, logic=positive.
[image: image160.png]‘Screen Editar

S
=
=

Property [Lamn]

Position Data setting Display

x [ || Pk Type Shape.

3] s Square ~)

AENE

Address Logc
Style w0 3 osiive

I™ Dauble





5. Make Screen 4 “Motor Setting”
As stated above, create the Screen 4. The input the text “Target”, “Current”, “Motor”,      “Speed” in proper place in the screen as in the following diagram: 
[image: image161.png]



    Select “Register” under “Object” menu or click [image: image162.png]


 in the tool bar. Move the mouse to proper place under “Target” and click the left key of the mouse to confirm. Then set the parameter of the register, Address=D80, Digits=5, Decimal=1, Mode=Dec. Select the “Set” check box as shown in the following diagram: 
[image: image163.png]Sereen Editor

Property [ Numeric |

Position Format Data setting
« ETE | 2ot PLC Address Max input
= 12 2] W set ==
v o 3 | Deema Type I~ Password  in input
L[ D x I Limite. TE]
Style Data type Address o =] Eng: Max
€ HexjB B0 = ==
I™ Double

QbE Registers Eng. min

I~ Reverse I™ Signed L[ =




    Select “Register” under “Object” menu or click [image: image164.png]


 in the tool bar. Move the mouse to proper place under “Current” and click the left key of the mouse to confirm. Then set the parameter of the register, Address=D90, Digits=5, Decimal=1, Mode=Dec. Don’t select the “Set” check box as shown in the following diagram: 
                [image: image165.png]Screen Editor

Property [ Numeric ]

CEEEE | e s
Y s 4] | Decimal Type - Min input
= o~ I~ Limite =]
Style Data type: Address [orignal =] Eng. Max
© HEX/BCD TS ==E
I” Double

& DEC Registers Eng. min

I Reverse || Sioned = 2




6. Make Screen 5 “Alarm List”
Click [image: image166.png]


 in the tool bar. A prompting dialogue frame as the following will be show. Set the initial coil type as M88 first. And the alarming information for M88 is “Be abnormal for unit1”; the alarming information for M89 is “Be abnormal for unit 2”; the alarming information for M90 is “Be abnormal for unit 3”; as shown in the following diagram:
[image: image167.png][

REFURRIAE
RS -
ERE I TR B R
52 | #m BENE
o [Be brormal for unit 1
1 e bnormal for unit 2
B abnormal for unit 3|
B
s A

s

Bl





Click “OK” to confirm. Thus the whole control file of the drying box system is finished. Then click “Save Project “
7. Download the drying box project data into SH-300.

Manipulation                                  3
3.1 Download Window

1. Connect the operating unit interface to the configuration computer using a SH-PC cable.
2. Confirmed SH-300 has added on the DC24V power source.
3. Press [image: image168.png]e



and start to download the date, the screen appears the downloading picture prompt frame.
[image: image169.png]Compie.

‘Download.

Cancel





[image: image170.png]


 Note : Don’t cut off the power supply when SH-300 is receiving data from the configuration computer.

3.2 Communication
When you finished the downloading of the project data file, cut off the power supply and remove the communication cable SH-PC. Connect SH-300 to PLC with a communication cable and check the setting of PLC communication parameters. Meanwhile add the DC24V power to PLC and SH-300.Then SH-300 will enters the normal operation condition.
[image: image171.png]



[image: image172.png]


 Note: when SH-300 communicates with PLC, the initial window appears as shown above. Please press “∧”key or “∨”key the system will be normal. If the system isn’t normal you should check the communication of SH-300 and PLC. 
3.3 Shifting the windows
Take the project windows of the drying boxes as an example to introduce the manipulation of SH-300.

SH-300 displays window No.1 at first (the initial window is No.1).
[image: image173.png]DryingboxControlMenu:
@D Temnp @ State @Motor




Window No.1 is a main menu window. Pressing ① switch to the window of temperature setting(No.2) that is shown as follows: 
[image: image174.png]""" Target :: Current

Termp 80,007 60.58T




3.4 System Password
After setting system password, you must input the password before you change the data. Then press “SET” key ,it will appear the picture as follows :
[image: image175.png]



Select “1 ,LOGIN”  “2.LOGOUT” or “EXIT” with Up, Down keys and then press “ENT”  
Select “1 ,LOGIN” the window will display as follows:
(select 2 to logout, select 3 to exit the window.)

[image: image176.png]CINPUT PASSWORD -





Input the password (0-999999), which is shown as”*”. Press ENT. If password is correct, it will show the window as follows:

[image: image177.png]- LOGIN SUCCESS - - -




If password is incorrect, it will show the window as follows:

[image: image178.png]- PASSWORD ERROR - -

- PRESS ANY KEY





Then press ENT,return to the password window.

Select “2 ,LOGOUT” and Press ENT it will show the window as follows:
[image: image179.png]- LOGOUT SIUCCESS - -
. PRESS ANY KEY. - - -





3.5 Data setting
When SH-300 display NO.2 picture press SET key and the setpoint of work temperature is flickering, you can change the cursor position by pressing “＜” and ”＞”and change setpoint by pressing “∧” and “∨”.
Press ENT to confirm the input data, the data has been written into PLC register D100, and the data will be normally displayed and not flickering. Press ENT to enter the setting mode again
3.6 State Monitoring
After finished the setting of register, press “∧” and return to the main menu ,SH-300 is shown as follows:
[image: image180.png]DryingboxControlMenu:
@D Temnp @ State @Motor




Press ② enter the window of state monitoring (No.3), which is shown as follows:
[image: image181.png]Heating Unit 1 °

Heating Unit 3¢





SH-300 will display the state monitoring window for three group heating units. When a heating unit is running the indicator will be show as full state and operator can monitor the running state of the heating units by the window.


Connection with PLC                 4
4.1 Mitsubishi FX Series   

SH-300 can communicate with the programming port of all types of Mitsubishi FX series PLC or the FX2N-422BD module of the FX2N series.

SH-300 software configuration:

	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port/ FX2N-422BD

	Default parameter
	9600bps、7bits、1stop、Even

	Station No.
	1(1 is fixed and can’t be changed)

	Distance (Max.)
	70m

	Communication mode
	RS422/ Programming port

	Cable type
	Special cable/SC09

	PLC series
	FX0S
	FX0N
	FX2N

	Inner relay address
	M000-M511
	M000-M511
	M0000-M3071

	Register address
	D00-D31
	D000-D255
	D0000-D7999


Connection guidance of Special cable
	SH-300 side
	2 RXD
	
	2 RXD
	PLC side

	9 pin D shape
	3 TXD
	
	4 TXD
	8pinRound shape

	Female plug
	5 GND
	
	1 GND
	male plug

	
	
	
	7 GND
	


\] [image: image182.png]


                                                                  

[image: image183.png]


Note: In order to insure the normal communication you must use SC09 when you select the programming cable of the FX series 

4.2 Siemens S7-200 Series
SH-300 can communicate with the programming port or external communication port of Siemens S7-200 series through PPI protocol.

SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	RS485 COM port

	PLC COM port
	Programming port/ external communication port

	Default parameter
	9600bps、8bits、1stop、Even

	Station No.
	2-126 ,2 is Windows default 

	Distance (Max.)
	100m (twisted-pair)

	Communication mode
	RS485

	Cable type
	Special cable

	Inner relay address
	M0.0-M31.7

	Register address
	VW0000-VW5118


Connection guidance of Special cable

	
	1 TD+
	
	
	

	SH-300 side
	9 RD+
	
	3  A
	PLC side

	9 pin D shape


	6 TD-
	
	8  B
	9 pin D shape



	Female plug
	8 RD-
	
	
	male plug


( when SH-300 communicates with S7-200 series PLC you are recommended to use the program the programming cable )

4.3 OMRON C Series
SH-300 can communicate with the programming port of CQM、CPM series PLC through HOST-Link protocol. 
SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port/ external communication port

	Default parameter
	9600bps、7bits、2stop、Even

	Station No.
	0-99 ,0 is Windows default 

	Distance (Max.)
	15m 

	Communication mode
	RS232

	Cable type
	Special cable

	Inner relay address
	IR200.0-IR231.F(IR2000.0-IR231.15)

	Register address
	DM000-DM1024


Note: Because CQM-CPU11 and CAPM1A have only one COM port. you must use the programming cable or the CIF01-CAB Communication module of the OMRON communicating with SH300
Connection guidance of Special cable
	SH-300 side 
	2 RXD
	
	2 TXD
	PLC side

	9 pin D shape
	3 TXD
	
	3 RXD
	9 pin D shape

	Female plug
	5 GND
	
	9 GND
	male plug


Note: the register won’t be set unless the CPU must work in the monitor mode
4.4 Delta DVP Series
SH-300 can communicate with the delta DVP series PLC, the communication port is the programming port of PLC 

SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port

	Default parameter
	9600bps、7bits、1stop、Even

	Station No.
	1-254 ,1 is Windows default 

	Distance (Max.)
	15m 

	Communication mode
	RS232

	Cable type
	Special cable

	Inner relay address
	M0-M1270

	Register address
	D0-D1066


Connection guidance of Special cable:

	SH-300 side
	2 RXD
	
	5 TXD
	PLC side

	9 pin D shape
	3 TXD
	
	4 RXD
	9 pin D shape

	Female plug
	5 GND
	
	8 GND
	Male plug


( when SH-300 communicates with Delta DVP series PLC you are recommended to use the the programming cable )
4.5 Panasonic FP Series
SH-300 can communicate with Panasonic FP series PLC, the communication port is the programming port of PLC or external communication port.

SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port

	Default parameter
	9600bps、8bits、1stop、0dd

	Station No.
	1-32 ,1 is Windows default 

	Distance (Max.)
	15m 

	Communication mode
	RS232

	Cable type
	Special cable

	Inner relay address
	R0000-R875F

	Register address
	DT0000-DT6134


Connection guidance of SH-CAB-FP0 :
	
	2 RXD
	
	2 TXD
	

	SH-300 side
	3 TXD
	
	3 RXD
	PLC side

	9 pin D shape
	5 GND
	
	7 GND
	9 pin　D shape

	Female plug
	
	
	4
	Male plug

	
	
	
	5
	

	
	
	
	8
	

	
	
	
	9
	


Connection guidance of SH-CAB-FP1 :
	SH-300 side
	2 RXD
	
	2 TXD
	PLC side

	9 pin D shape
	3 TXD
	
	3 RXD
	5 pin　D shape

	Female plug
	5 GND
	
	１GND
	Male plug


[image: image184.png]



( when SH-300 communicates with Panasonic FP series PLC you are recommended to use the the programming cable )
4.6 Vigor VH Series
SH-300 can communicate with Vigor VH series PLC, the communication port is the Programme device assistant port of PLC
SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port

	Default parameter
	19200bps、7bits、1stop、Even

	Station No.
	0-255 ,0 is Windows default 

	Distance (Max.)
	15m 

	Communication mode
	RS232

	Cable type
	special cable

	Inner relay address
	M0-M5119

	Register address
	D0-D8191


Connection guidance of special cable
[image: image185.png](0%

=]




                  [image: image186.png]G217




	SH-300 side
	2 RXD
	
	2 RXD
	PLC side

	9 pin D shape

Female plug
	3 TXD
	
	3 TXD
	USB male plug

	
	5 GND
	
	4 GND
	


[image: image187.png](DB

s——{i



                       [image: image188.png]4321



 

	SH-300 side
	2 RXD
	
	2 RXD
	PLC side

	9 pin D shape

Female plug
	3 TXD
	
	3 TXD
	JST 4P 4pin

Female plug

	
	5 GND
	
	4 GND
	


( when SH-300 communicates with Vigor VH series PLC you are recommended to use the  programming cable )
4.7 Koyo S Series
SH-300 can communicate with Koyo S series PLC, the communication port is the programming port of PLC 

SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port

	Default parameter
	9600bps、8bits、1stop、0dd

	Station No.
	1-99 ,1 is Windows default 

	Distance (Max.)
	15m 

	Communication mode
	RS232

	Cable type
	MD2-SZ applies to SZ、SH、SH series
MD2-SG applies to SU、SG series

	Inner relay address
	M000-M377

	Register address
	R2000-R7777


Connection guidance of MD2-SZ:
	
	
	
	1 GND
	

	
	2 RXD
	
	
	

	SH300 side
	3 TXD
	
	3 RXD
	PLC side

	9PIN D shape
	
	
	4 TXD
	（6PIN）

	Female plug
	
	
	
	

	
	5 GND
	
	6 GND
	



 [image: image189.png]



Connection guidance of MD2-SG:
	
	2 RXD
	
	2 TXD
	

	SH300 side
	3 TXD
	
	3 RXD
	PLC side

	9PIN D shape
	
	
	4 RTS
	（25PIN）

	Female plug
	
	
	5 CTS
	

	
	5 GND
	
	7 GND
	


( when SH-300 communicates with Koyo S series PLC you are recommended to use the programming cable )
4.8 ADC DL05 Series
SH-300 can communicate with ADC DL05 series PLC, the communication port is the programming port of PLC., In order that the SH300 can communicate with ADC DL 05 series communication Port2 normally, ADC PLC must be correspondingly configured. To do this, the ADC Communication Protocol must be defined with the DirectSoft software, Select the “SETUP” submenu under “PLC” option in the DirectSoft ,Set up Communication Ports according to the picture indicated below.
[image: image190.png]Setup Communication Ports
Port: | Port 2 Close I

Protocol: K-sequence W] >0

DirectNET
MODBUS Help
Non-sequence

Timeout: | 800 m§

oox0O

RTS ON Delay Time: | 5mS

RTS OFF Delay Time: | 2mS ﬂ
Station Number: | 1 g

Baud Rate: | 38400

Stop Bits: | 1

Parity: | None

Format: | Hex





SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port

	Default parameter(port1)

Default parameter(port2)
	9600bps(fixed)、8bits、1stop、0dd(fixed)

300-38400bps, 8bits、1stop、0dd(default)

	Station No.(port1)

Station No.(port2)
	1 (1 is fixed and can’t be changed)
1-99 ,1 is Windows default 

	Distance (Max.)
	15m 

	Communication mode
	RS232

	Cable type
	Special cable

	Inner relay address
	M0-M777

	Register address
	R0-R7777


Connection guidance of port 1 special cable：
	SH-300 side
	2 RXD
	
	3 RXD
	

	9 pin D shape

Female plug
	3 TXD
	
	4 TXD
	PLC side

	
	5 GND
	
	1 GND
	（6PIN port1）


[image: image191.png]



( when SH-300 communicates with ADC DL05 series PLC you are recommended to use the the programming cable )
4.9 FATEK FBs Series
SH-300 can communicate with FATEK FBs series PLC the communication port is the port 0 of PLC 

SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port

	Default parameter
	9600bps、7bits、1stop、Even

	Station No.
	1-254 ,1 is Windows default

	Distance (Max.)
	15m

	Communication mode
	RS232

	Cable type
	Special cable

	Inner relay address
	M0000-M2001

	Register address
	R0000- R3839.R5000-R8071


Connection guidance of Special cable

	SH-300 side
	2 RXD
	
	3 TXD
	PLC side

	9 pin D shape
	3 TXD
	
	1 RXD
	4 pin round shape

	Female plug
	5 GND
	
	2 GND
	Male plug


                                                  [image: image192.png]



(when SH-300 communicates with FATEK series PLC you are recommended to use the programming cable )
4.10 Schneider NEZA/TWIDO Series
SH-300 can communicate with Schneider NEZA/TWIDO Series PLC through Modbus RTU protocol, the communication port is the programming port of PLC 

SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	RS485 COM port

	PLC COM port
	Programming port

	Default parameter
	19200bps、8bit、1stop、Even

	Station No.
	1－247，1 is Windows default

	Distance (Max.)
	100m（twisted-pair）

	Communication mode
	RS485

	Cable type
	Special cable

	Inner relay address
	%M000-%M256

	Register address
	%MW0-%MW2999


Connection guidance of Special cable

	
	5GND
	
	5GND
	

	SH-300 side
	1 TD+
	
	
	PLC side

	9 pin D shape
	9 RD+
	
	1  A
	8pin Round shape

	Female plug
	6 TD-
	
	2  B
	male plug

	
	8 RD-
	
	5
	

	
	
	
	7
	


[image: image193.png]



(when SH-300 communicates with Schneider NEZA/TWIDO Series PLC you are recommended to use the programming cable the switch on which is placed “3” position)
4.11 AB (AB-DF1 protocol) Series

SH-300 can communicate with the Allen-Bradley series PLC via AB-DF1 Protocol, the communication port is the programming port of PLC 

SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port

	Default parameter
	9600bps、8bits、1stop、None

	Station No.
	1 (1 is fixed and can’t be changed)

	Distance (Max.)
	15m 

	Communication mode
	RS232

	Cable type
	Special cable

	Inner relay address
	B3/9/10/11/12/13:  0-254

	Register address
	N7/9/10/11/12/13/14/15: 0-254


Connection guidance of Special cable

	
	2 RXD
	
	4 RXD
	

	SH-300 side
	3 TXD
	
	7 TXD
	PLC side

	9 pin D shape
	
	
	
	8pin Round shape

	Female plug
	
	
	
	male plug

	
	5 GND
	
	2 GND
	


                                                  [image: image194.png]



(when SH-300 communicates with Allen-Bradley (AB-DF1 Protocol) series PLC you are recommended to use the programming cable )
4.12 THINGET XC Series

SH-300 can communicate with THINGET XC series PLC, the communication port is the programming port of PLC 

SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port

	Default parameter
	19200bps、8bits、1stop、Even

	Station No.
	0－255，1 is Windows default

	Distance (Max.)
	15m 

	Communication mode
	RS232

	Cable type
	Special cable

	Inner relay address
	M0-M7999

	Register address
	R0-R7999


Connection guidance of Special cable

	
	2 RXD
	
	4 RXD
	

	SH-300 side
	3 TXD
	
	5 TXD
	PLC side

	9 pin D shape
	
	
	
	8pin Round shape

	Female plug
	
	
	
	male plug

	
	5 GND
	
	8 GND
	


                                        [image: image195.png]



(when SH-300 communicates with THINGET series PLC you are recommended to use the programming cable )
4.13 Emerson EC20 Series

SH-300 can communicate with Emerson EC20 series PLC, before communication with SH-300 PLC need to be configured .setup port0 of PLC as Modbus communication protocol.
SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port

	Default parameter
	19200bps、8bits、1stop、Even

	Station No.
	0－255，1 is Windows default

	Distance (Max.)
	15m 

	Communication mode
	RS232

	Cable type
	Special cable

	Inner relay address
	M0-M1999 Y0-Y377(O)

	Register address
	D0-D7999 T0-T255


Please consult Emerson PLC user manual for particular address
Connection guidance of Special cable

	
	2 RXD
	
	4RXD
	

	SH-300 side
	3 TXD
	
	5TXD
	PLC side

	9 pin D shape
	
	
	
	8pin Round shape

	Female plug
	
	
	
	male plug

	
	5 GND
	
	3 GND
	


                                        [image: image196.png]




(when SH-300 communicates with Emerson EC20 series PLC you are recommended to use the programming cable )

4.14 HITACHI MICRO-EH Series

SH-300 can communicate with HITACHI MICRO-EH series PLC, the communication port is the programming port of PLC 

SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port

	Default parameter
	19200bps、7bits、1stop、Even

	Station No.
	0 (0 is fixed and can’t be changed)

	Distance (Max.)
	15m 

	Communication mode
	RS232

	Cable type
	Special cable

	Inner relay address
	R0-R7BF M0-M3FFF

	Register address
	WR0-WRFFF WM0-WM3FFF


Connection guidance of Special cable:

	
	
	
	1 GND
	

	SH-300 side
	2 RXD
	
	2
	PLC side

	9 pin D shape
	3 TXD
	
	5 RXD
	6PIN

	Female plug
	5 GND
	
	6 TXD
	

	
	
	
	7
	




(when SH-300 communicates with HITACHI MICRO-EH series PLC you are recommended to use the programming cable )
4.15 KDN-K3 Series

SH-300 can communicate with KDN-K3 series PLC, the communication port is the programming port of PLC 

SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port

	Default parameter
	9600bps、8bits、1stop、None

	Station No.
	1－31，1 is Windows default

	Distance (Max.)
	15m 

	Communication mode
	RS232

	Cable type
	Special cable

	Inner relay address
	I0.0-I7.7/ Q0.0-Q7.7/ M0.0-M31.7

	Register address
	AIW0-62/AQW0-62/AQW0-4094


Connection guidance of Special cable:

	SH-300 side
	2 RXD
	
	2 RXD
	PLC side

	9 pin D shape
	3 TXD
	
	3 TXD
	9 pin D shape

	Female plug
	
	
	
	Male plug

	
	5 GND
	
	5 GND
	


( when SH-300 communicates with KDN-K3 series PLC you are recommended to use the programming cable )
4.16 MODBUS RTU/ASCII and RTU/ASCII EXTEND protocol

1. Introducing Modbus Protocol
SH-300 communicates by using a master–slave technique, in which one SH-300(the master) can send query message. one programmable controller(the slave) responds according to the requested data supplied by SH-300. The Modbus protocol establishes the format for the master’s query by placing into it the device address, a function code, any data to be sent, and error–checking field. The slave’s response message is also constructed by using Modbus protocol. It contains fields confirming the action taken, any data to be returned, and an error–checking field. The returned data bytes contain the data collected by the slave, such as register values or coil status. If error occurred in receipt of the message, or if the slave is unable to perform the requested action, the slave will construct an error message and send it as its response.
2. MODBUS RTU/ASCII and RTU/ASCII EXTEND communication parameter configuration:

	Item
	content

	SH-300 COM port
	9 pin COM port

	Default parameter (RTU)
	Consistent with PLC Port

	Default parameter (ASCII)
	Consistent with PLC Port

	Station No.
	1-247,1 is windows default

	Protocol
	MODBUS RTU/ASCII, RTU/ASCII EXTEND

	Distance (Max.)
	15m/100m (twisted-pair)

	Communication mode
	RS232/485/422

	Cable type
	MODBUS-RS232/485/422

	Coil variable address type
	0X

	Discrete variable address type
	1X

	Register variable address type
	3X/4X/5X/6X 


3. Connection guidance of Special cable
MODBUS-RS232 

	SH-300 side
	2RXD
	
	TXD
	slave device

	9 pin D shape
	3 TXD
	
	RXD
	side

	Female plug
	5GND
	
	GND
	


MODBUS-RS485 

	
	1 TD+
	
	RD+
	

	SH-300 side 
	9 RD+
	
	TD+
	Slave device

	9 PIN D shape 
	6 TD-
	
	RD-
	side

	Female plug
	8 RD-
	
	TD-
	

	
	5 GND
	
	GND
	


MODBUS-RS422 

	
	1 TD+
	
	RD+
	

	SH-300 side
	9 RD+
	
	TD+
	slave device

	9 pin D shape
	6 TD-
	
	RD-
	side

	Female plug
	8 RD-
	
	TD-
	

	
	5GND
	
	GND
	


4. The list of corresponding relationship between address type of SH-300 and function codes in Modbus RTU/ASCII Protocol

	Object type
	Address type
	Function 
code
	R/W
	Description

	Indicator
	0x
	0x01
	Read
	Read coils ON/OFF status 

	
	1x
	0x02
	Read
	Read discrete input

	Function Key
	0x
	0x05
	Write
	Write coils ON/OFF status 

	Dynamic text
	3x
	0x04
	Read
	Read input register

	
	4x
	0x03
	Read
	Read holding register

	Register
	3x
	0x04
	Read
	Read input register

	
	4x
	0x03
	Read
	Read holding register

	
	
	0x06
	Write
	Write single holding register

	
	
	0x10
	Write
	Write double holding register

	Bar graph/     Trend  graph
	3x
	0x04
	Read
	Read input register

	
	4x
	0x03
	Read
	Read holding register


5. The list of corresponding relationship between address type of SH-300 and function codes in Modbus RTU/ASCII EXTEND Protocol

	
	Object type
	Address type
	Function code
	R/W
	Description

	
	Indicator
	0x
	0x01
	Read
	Read coils ON/OFF status

	
	
	1x
	0x02
	Read
	Read discrete input

	
	
	3x_bit
	0x04
	Read
	Read one bit of input register value  

	
	
	4x_bit
	0x03
	Read
	Read one bit of holding register value

	
	Function Key
	0x
	0x05
	Write
	Write coils ON/OFF status 

	
	
	4x_bit
	0x06
	Write
	Write one bit of single holding register value  

	
	
	
	0x10
	Write
	Write one bit of double holding register value  value value

	
	Dynamic text
	3x
	0x04
	Read
	Read input register

	
	
	4x
	0x03
	Read


	Read holding register

	
	
	5x
	
	
	

	
	
	6x
	
	
	

	
	Register
	3x
	0x04
	Read
	Read input register

	
	
	4x
	0x03
	Read
	Read holding register

	
	
	
	0x06
	Write
	Write single holding register 

	
	
	
	0x10
	Write
	Write double holding register 

	
	
	5x
	0x03
	Read
	Read holding register

	
	
	
	0x06
	Write
	Write single holding register 

	
	
	
	0x10
	Write
	Write double holding register 

	
	
	6x
	0x03
	Read
	Read holding register

	
	
	
	0x06
	Write
	Write single holding register 

	
	Bar graph/ Trend  graph
	3x
	0x04
	Read
	Read input register

	
	
	4x
	0x03
	Read
	Read holding register

	
	
	5x
	
	
	

	
	
	6x
	
	
	


Note:
1. When selecting “3x” as register address type, single or double register only can be read, not to be written.
2. When selecting “4x” as register address type to read or write double register. the first byte contains the high order bit and the second contains the low order bit.
3. When selecting “5x” as register address type to read or write double register. The first byte contains the low order bit and the second contains the high order bit.
4. When selecting “6x” as register address type, only single register can be read or written 
5.”bit” expresses the bit address of Register value. It is in the range of”0~F”. The register value is expressed as the data of sixteen bit binary. Each bit expresses one coil status. Status is indicated as: 1 = ON, 0 = OFF. 

         6. when selecting “4x_bit” as address type of function key , one bit of register value can be set  “0” or “1’”. (single or double Register).
6. Parameter setting in the SH-300 software
6.1 Consult PLC user manual about setting communication port parameter in Modbus protocol. Click “Set plc type” under “Connect” option, and set the SH-300 communication parameter. In order to communicate with the PLC normally, the communication parameter of SH-300 must be consistent with that of PLC.
[image: image197.png]|_sevpictypecen.. el

[ Target PLC/Ccontroller Type

pLC

-Commurication settings

sadrte [0 =
s b =
e
ity =

ok Cancel





6.2 Consult PLC user manual and work out the data address accurately. Different type PLC uses different method of calculating data address. The following examples will introduce the operation of some coils and registers with SH-300 software in MODBUS protocol.
6.2.1 Here is an example of setting coil M15 status

Use the function key “[image: image198.png]


” to set coil M15 status. According to “the list of corresponding relationship between address type and function codes in Modbus Protocol” the address type of setting coil status is “0X”. Inner coil(M) address is in the range of M0-M512(D). MODBUS data address is in the range of 3072-3583. The corresponding MODBUS data address of M15 is 3087.

[image: image199.png]rty [Touch button]

ion Touch button—| ~Action: Set Coll
6 2 Key « set Coil PLC Address Type
2 - 1 = X [
G T | PV SR )
Address
I~ Hand C SetRegister  |[3087 =)
uble
I~ Irwisiole
verse I™ Password

 oFF




When SH-300 set coil 15 the data format to be send from SH-300 is shown as following.
	Query message

	Field Name
	Example (Hex)

	Device address
	-

	Function code 
	05

	Coil address Hi  
	0C

	Coil address Lo

	0F

	Set data Hi    
	FF

	Set data Lo
	00

	CRC Lo
	-

	CRC Hi
	-


The query message specifies the coil to be set. The requested ON/OFF state is specified by a constant in the query data field. A value of FF 00 hex requests the coil to be ON. A value of 00 00 requests it to be OFF. All other values are illegal and will not affect the coil.

Response: The normal response is an echo of the query, returned after the coil state has been set.
6.2.2 Here is an example of reading coils M15

Use indicator ”[image: image200.png]


” to indicate coil M15 status. According to “the list of corresponding relationship between address type and Function Codes in Modbus Protocol” the address type of reading coil status is “0X”. The corresponding MODBUS data address of M15 is 3087.
[image: image201.png]Screen Editor

Property [Lamp]

Position Data setting Display
x [ T3] || PLcAddress Type Shape
1 = ox Round ~]

Adhess Logic

v[= =
Sty [ & = ositive

I™ Dauble





When SH-300 read coil M15 the data format to send from SH-300 and responded by PLC is shown as following.
	Query message
	 
	response message

	Field Name
	Example (Hex)
	
	Field Name
	Example (Hex)

	Device address
	-
	
	Device address
	-

	Function code 
	01
	
	Function code 
	01

	Coil starting address Hi   
	0C
	
	The count of return bytes
	01

	Coil starting address Lo

	0F
	
	Data  (Coil M22-M15)
	-

	No. of Coil Hi           
	00
	
	CRC Lo
	-

	No. of Coil Lo
	01
	
	CRC Hi
	-

	CRC Lo
	-
	
	
	

	CRC Hi
	-
	
	
	


The coil status in the response message is packed as one coil per bit of the data field. Status is indicated as: 1 = ON; 0 = OFF. The LSB of the data byte contains coil M15 addressed in the query. The highest order end of this byte contains coil M22.
“1X” expresses reading discrete input .For example PLC input signal, inner special coil status etc.

6.2.3. Here is an example of displaying and setting Register R1088

According to “the list of corresponding relationship between the address type and function codes in Modbus Protocol” the address type of reading and writing holding register is “4X” ,The holding register address is in the range of R0-R3839. Modbus address is in the range of 0-3839. the corresponding Modbus data address of register R1088 is 1088.

[image: image202.png]Screen Editor

12345

12345

Property [ Numeric |

Postion Format Data setting
« B Do PLC Adhess Max input
=3 I = I set |
Y [ Beomel Type o Min nput
I Cunte [ 3]
styie Data type o] En. Max
& HEX/BCD 3 e
I” Double Joss ™ =] =

 DEC Eng. min

Regiters
I Reverse || i 3] 2




When SH-300 read holding register the data format to be send from SH-300 and responded by PLC is shown as following.

	Query message
	 
	Response message

	Field Name
	Example(Hex)
	
	Field Name
	Example(Hex)

	Device address
	-
	
	Device address
	-

	Function code 
	04
	
	Function code 
	04

	Register starting address Hi   
	04
	
	The count of return bytes
	02

	Register starting address Lo

	40
	
	Data Hi (Register R1088)
	-

	No. of registers Hi           
	00
	
	Data Lo (Register R1088)
	-

	No. of registers Lo
	01
	
	CRC Lo
	-

	CRC Lo
	-
	
	CRC Hi
	-

	CRC Hi
	-
	
	
	


When SH-300 write holding register the data format to be send from SH-300 is shown as following.

	Query message

	Field Name
	Example (Hex)

	Device address
	11

	Function code 
	06

	Register address Hi  
	00

	Register address Lo

	01

	Set data Hi    
	00

	Set data Lo
	03

	CRC Lo
	-

	CRC Hi
	-


Response :The normal response is an echo of the query, returned after the register contents have been written.
Note:

1. If the communication parameter is not correct. SH-300 will not communicate with PLC normally.

2. If the data address you input is not in the range that is specified by user manual. SH-300 will not communicate with PLC normally.

3. If PLC don’t support the address type you select (For example Delta PLC don’t support “3X”). SH-300 will not communicate with PLC normally.

4.17 SH-300 Freedom Protocol
1. Communication configuration
SH-300 can communicate with some controllers via freedom protocol. When SH-300 communicates with controller via this protocol user need to define own controller freedom communication format first. Here SH-300 is a master, controller is a slave. The request message is sent from SH-300 and controller makes response message. Communication parameter is shown as followIing:

[image: image203.png]Jil=i )

Target PLC/Ccontraller Type

e E
Coricston etings

o
.
e
v |

ok Cancel





	Item
	Content

	SH-300 COM port
	9 pin COM port

	Controller COM port
	Programming port

	Default parameter
	9600bps、8bits、1stop、None

	Station No.
	1-254 ,1 is Windows default

	Distance (Max.)
	15m/100m（twisted-pair）

	Communication mode
	RS232/485/422

	Cable type
	FREE-RS232/FREE-RS485/FREE-422


The freedom communication protocol takes byte as least addressing unit. And the most addressing is in the range of 0-FFFFFFFF. The value of Register is stored with byte value. For each Register, the first byte contains the high order bits and the second byte contains the low order bits. Simultaneously one byte can be expressed as an eight-bit binary value which shows each status of the 8 coils respectively. For example the Register B0 contains eight coil address(M0-M7). That’s to say if you change the status of coil M0 up to M7. the value of Register has been changed too. and if you change the value of Register ,the status of coil M have been changed too. Therefore when you use this protocol you need to distribute the address between Register and coil.   

If Registers are addressed starting at B0, W0, DW0. Allocation map of memory address is shown as following:

	Register
address
	Double

word 
	DW0
	DW4
	……

	
	word
	W0
	W2
	W4
	W6
	……

	
	byte
	B0
	B1
	B2
	B3
	B4
	B5
	B6
	B7
	……

	Coil address
	M0

∣
M7
	M8

∣
M15
	M16

∣
M23
	M24

∣
M31
	M32

∣
M39
	M40

∣
M47
	M48

∣
M55
	M56

∣
M63
	……
……


If Registers are addressed starting at B1, W1,DW1. Allocation map of memory address is shown as following:

	Register
address
	Double

word 
	DW1
	DW3
	……

	
	word
	W1
	W3
	W5
	W7
	……

	
	byte
	B1
	B2
	B3
	B4
	B5
	B6
	B7
	B8
	……

	Coil address
	M8

∣
M15
	M16

∣
M23
	M24

∣
M31
	M32

∣
M39
	M40

∣
M47
	M48

∣
M55
	M56

∣
M63
	M64
∣
M71
	……
……


Example: Write the double word values of 075BCD15 into Register DW0, the value of per byte is distributed as following:

	The address of double word
	DW0

	The address of word
	       W2
	W0

	The address of byte
	B 3
	B2
	B1
	B0

	set value
	07
	5B
	CD
	15


The value of DW0 is 075BCD15 when Register is addressed as double word. The value of W0 is CD15, W2 is 075B when Register is addressed as word. The value of B0 is 15, B1 is CD, B2 is 5B, B3 is 07 when Register is addressed as byte.

2. Connection guidance of special cable
FREE-RS232 

	SH-300 side 
	2 RXD
	
	TXD
	

	（9 PIN D shape ）
	3 TXD
	
	RXD
	Slave device

	Female plug
	5GND
	
	GND
	 side


FREE-RS485
	
	1 TD+
	
	RD+
	

	SH-300 side 
	9 RD+
	
	TD+
	Slave device

	（9 PIN D shape ）
	6 TD-
	
	RD-
	side

	Female plug
	8 RD-
	
	TD-
	

	
	5 GND
	
	GND
	


FREE-RS422
	
	1 TD+
	
	RD+
	

	SH-300 side 
	9 RD+
	
	TD+
	Slave device

	(9PIND shape)
	6 TD-
	
	RD-
	side

	Female plug
	8 RD-
	
	TD-
	

	
	5 GND
	
	GND
	


3. The data format of query from SH-300 and response from PLC
When SH-300 communicates with controller via freedom protocol the Register data and the status of inner coils can be set up by SH-300 and displayed on the SH-300 at real time. PC can be taken as dummy controller to communicate with SH-300. Here PC displays not only the Register data and the status of inner coils but also the data PC receives and sends during communicating with SH-300. In order to validate the communication between SH-300 and PC in time. Take the communication between SH-300 and PC as an example to introduce the data format of query from SH-300 and response from controller in freedom communication protocol.

1. Read single Coil Status M (0x40) 

Use this function code to read the status of single coil in controller. The query message specifies coil address. Coil status is indicated as: 01 = ON; 00 = OFF in the response message
Here is an example of reading the status coil M25 (0X40)

a. Make the screen displayed as following, use function key [image: image204.png]


 to set the status of coil M25
[image: image205.png]Sereen Editor

Praperty [Touch button]

Posiion

X [

Y a3
Style
I™ Double

I™ Reverse

“Touch button
Key

Left -

I™ Hand
I Invisble

I™ password

Action
© set col

€ Jump to

€ Set Register

set Col
PLC Address

1 =

Address
s 2

Con
 oFF

Type

T

 Reverse




b. Connect SH-300 with PC by using a SH-PC cable, download the screen into SH-300
c. click “[image: image206.png]


”to enter simulation state，use indicator to indicate the coil status 
[image: image207.png]Datalist

42:  PC RECEIVE: 55 55 01 40 00 00 00 00 00 00 19 00 00 00 00 00 04
4 PC SEND : 55 55 FF 01 40 00 00 00 00 00 00 19 01 00 00 00 04





[image: image208.png]Datalist

0:  PC RECEIVE: 55 55 01 40 00 00 00 00 00 00 19 00 00 00 00 00 04
1: PC SEND : 55 55 FF O1 40 00 00 00 00 00 00 19 00 00 00 00 03




When reading coil M25 status the data format of query message from SH-300 and response message from controller is shown as following:

	Byte NO.
	Query format (controller receive)
	Example
	Response format (controller send)
	Example

	0
	Framing starting
	55
	Framing starting
	55

	1
	Framing starting
	55
	Framing starting
	55

	2
	Device address
	01
	Response status  
	FF

	3
	Function code 
	40
	Device address
	01

	4
	Address offset
	00
	The function code 
	40

	5
	Reserved byte
	00
	Addressing offset
	00

	6
	Reserved byte
	00
	Reserved byte
	00

	7
	Address high order bit (Hi byte)
	00
	Reserved byte
	00

	8
	Address high order bit (Lo byte)
	00
	Address high order bit (Hi byte)
	00

	9
	Address Low order bit (Hi byte)
	00
	Address high order bit (Lo byte)
	00

	10
	Address Low order bit (Lo byte)
	19
	Address Low order bit (Hi byte)
	00

	11
	Reserved byte
	00
	Address Low order bit (Lo byte)
	19

	12
	Reserved byte
	00
	The status message of one coil
	01/00

	13
	Reserved byte
	00
	Reserved byte
	00

	14
	Reserved byte
	00
	Reserved byte
	00

	15
	Reserved byte
	00
	Reserved byte
	00

	16
	Verify value
	04
	Verify value
	04/03


Description : 

The value of Register and coil address is stored as byte value. According to the value of the address first use address Low order bit, and then use address high order bit. For each address bit , The first byte contains the high order bits and the second byte contains the low order bits.   

The framing of query and response message contains seventeen bytes which is fixed .
Framing starting [55][55] :the value is fixed.

Addressing offset [00]: If coils M0 is addressed as 0 the address offset is [00], If coils M1 is addressed as 0 the address offset is [01],
Response status: 0x00 expresses error ,0xFF expresses right
Address low order bit: [00][19] expresses that the address of the coil to be read is 25 (D).
  The response state [FF] expresses normal response, [00] expresses abnormal response.

  Verify value: plus all bytes from framing starting byte to the penultimate byte, take the last byte of the summation as verify value.

2. Write Single Coil M (0x41)

Use this function code to setup ON/OFF state of single coil in controller
The ON/OFF state of requested coil is specified by a constant in the query data field. A value of FF 00 hex requests the coil to be ON. A value of 00 00 requests it to be OFF. Any other values are illegal and will not affect the coil.

Here is an example of writing coil M25 

use function key [image: image209.png]


 to set the coil status and use indicator to indicate it.
[image: image210.png]Datalist

82:  PC RECEIVE: 55 55 01 41 00 00 00 00 00 00 19 FF 00 00 00 00 04
3 PC SEND : 55 55 FF 01 41 00 00 00 00 00 00 19 00 00 00 00 04




 [image: image211.png]Datalist

52:  PC RECEIVE: 55 55 01 41 00 00 00 00 00 00 19 00 00 00 00 00 05
5: PC SEND : 55 55 FF 01 41 00 00 00 00 00 00 19 00 00 00 00 04





When writing coil M25 status the data format of query message from SH-300 and response message from controller is shown as following:
	Byte NO.
	Query format (controller receive)
	Example
	Response format (controller send)
	Example

	0
	Framing starting
	55
	Framing starting
	55

	1
	Framing starting
	55
	Framing starting
	55

	2
	Device address
	01
	Response status  
	FF

	3
	Function code 
	41
	Device address
	01

	4
	Address offset
	00
	Function code
	41

	5
	Reserved byte
	00
	Address offset
	00

	6
	Reserved byte
	00
	Reserved byte
	00

	7
	Address high order bit (Hi)
	00
	Reserved byte
	00

	8
	Address high order bit (Lo)
	00
	Address high order bit (Hi)
	00

	9
	Address Low order bit (Hi)
	00
	Address high order bit (Lo)
	00

	10
	Address Low order bit (Lo)
	00
	Address Low order bit (Hi )
	00

	11
	Coil status value。0xFF express M ON，0x00 express M OFF。
	FF/00
	Address Low order bit (Lo)
	19

	12
	Reserved byte
	00
	Reserved byte
	00

	13
	Reserved byte
	00
	Reserved byte
	00

	14
	Reserved byte
	00
	Reserved byte
	00

	15
	Reserved byte
	00
	Reserved byte
	00

	16
	Verify value
	04/05
	Verify value
	04


3. Read single byte of Register B（0X42）
Use this function code to read the value of single byte of Register in controller. The query message specifies the Register address. Registers are addressed starting at zero: Register 0 is addressed as 0.
4. Write single byte of Register B（0X43）
Use this function code to write the value into the single byte of Register in controller .The query message specifies the Register address and the value of single byte to be written. Registers are addressed starting at zero: Register 0 is addressed as 0
5. Read single Register W（0X44）
Use this function code to read the value of single Register in controller. The query message specifies the Register address. Registers are addressed starting at zero: Register 0 is addressed as 0. the Register data in the response message occupy two byte. the first byte contains the high order bits and the second byte contains the low order bits.

6. Write single Register W（0X45）
Use this function code to write the value into single Register in controller .The query message specifies the Register address and the value of single Register to be written. Registers are addressed starting at zero: Register 0 is addressed as 0
7. Read double Register DW（0X46）
Use this function code to read the value of double Registers in controller. The query message specifies the Register starting address. Registers are addressed starting at zero: Register 0 is addressed as 0. Each Register data in the response message occupy two byte. The first byte contains the high order bits and the second contains the low order bits.
Here is an example reading the value of Register 35 36

a. Make the screen displayed as the following:

[image: image212.png]Screen Editor

12345678

Property [ Numeric ]

Postion Format Data setting

e pcades Max nput

< ry v

g B 0 B z set o e 3

v [p 4] | Decmdl Type Pawad e
FE |ow = W Linite 6 =

|Original =

Style Data type- J— Eng. Max
- oot  HEX/BD = - 2
oute 2 E|

-
oeCc o Eng.min

Reverse | z 2



    [image: image213.png]A2BIC6D8

Datalist

160:  PC RECEIVE: 55 55 01 46 00 00 00 00 00 23 00 00 00 00 00 00 14
161: PC SEND : 55 55 FF O1 46 C6 D8 AZ B9 00 00 00 00 00 00 00 E9




When reading Register 35 36 the data format of query message from SH-300 and response message from controller is shown as following:
	Byte NO.
	Query format (controller receive)
	Example
	Response format (controller send)
	Example

	0
	Framing starting
	55
	Framing starting
	55

	1
	Framing starting
	55
	Framing starting
	55

	2
	Device address
	01
	Response status
	FF

	3
	Function code 
	46
	Device address
	01

	4
	Reserved byte
	00
	Function code
	46

	5
	Reserved byte
	00
	Register 35 data Hi 
	C6

	6
	Address high order bit (Hi)
	00
	Register 35 data Lo 
	D8

	7
	Address high order bit (Lo)
	00
	Register 36 data Hi 
	A2

	8
	Address Low order bit (Hi)
	00
	Register 36 data Lo 
	B9

	9
	Address Low order bit (Lo)
	23
	Reserved byte
	00

	10
	Reserved byte
	00
	Reserved byte
	00

	11
	Reserved byte
	00
	Reserved byte
	00

	12
	Reserved byte
	00
	Reserved byte
	00

	13
	Reserved byte
	00
	Reserved byte
	00

	14
	Reserved byte
	00
	Reserved byte
	00

	15
	Reserved byte
	00
	Reserved byte
	00

	16
	Verify value
	14
	Verify value
	E9


8. Write double Register DW（0X47）
Use this function code to write the value into two continuous Register in controller .The query message specifies the Register starting address and the data of double Register to be written. Registers are addressed starting at zero: register 0 are addressed as 0.

Here is an example of writing 2A6B8C9D hex into two Registers 58.59 in controller
a. Make the screen displayed as the following:

[image: image214.png]Screen Editor

12345678

Property [ Numeric ]

Positon Format Data setting

e = Ao M input

< 2 v

g B 0 B z set o e 3

v [ 4] | Decmal Type Pawad e
FE |ow = W Linite 6 =

|Original =

Style Data type- J— Eng. Max
I & HEX/BCD ] = =
ouble = E|

-
oEC — Eng. min

Reverse | z 2



      [image: image215.png]2A6B8C

Datalist

166:  PC RECEIVE: 55 55 01 47 00 00 00 00 00 34 8C 9D 2A 6B 00 00 EA
167: PC SEND : 55 55 FF 01 47 00 00 00 00 00 34 00 00 00 00 00 2B




When write 2A6B8C9D hex into two Registers 58 59 in controller the data format of query message from SH-300 and response message from controller is shown as following:
	Byte NO.
	Query format (controller receive)
	Example
	Response format (controller send)
	Example

	0
	Framing starting
	55
	Framing starting
	55

	1
	Framing starting
	55
	Framing starting
	55

	2
	Device address
	01
	Response status
	FF

	3
	Function code
	47
	Device address
	01

	4
	Reserved byte
	00
	Function code
	47

	5
	Reserved byte
	00
	Reserved byte
	00

	6
	Address high order bit (Hi)
	00
	Reserved byte
	00

	7
	Address high order bit (Lo)
	00
	Address high order bit (Hi)
	00

	8
	Address Low order bit (Hi)
	00
	Address high order bit (Lo) 
	00

	9
	Address Low order bit (Lo )
	3A
	Address Low order bit (Hi)
	00

	10
	Register 58 data Hi 
	8C
	Address Low order bit (Lo)
	3A

	11
	Register 58 data Lo 
	9D
	Reserved byte
	00

	12
	Register 59 data Hi 
	2A
	Reserved byte
	00

	13
	Register 59 data Lo 
	6B
	Reserved byte
	00

	14
	Reserved byte
	00
	Reserved byte
	00

	15
	Reserved byte
	00
	Reserved byte
	00

	16
	Verify value
	EA
	Verify value
	2B


9. Read a series of coils M （0X48）
Use this function code to read a series of coil status in controller. The query message specifies coil starting address .The quantity of coil status byte depends on the quantity of the coil to be read and the coil starting address, N=(the coil number + the coil starting address)/8  if the remainder is unequal to zero N=N+1, Coil status [Data 1]….. [Data N]: each bit of byte indicate one coil status .In which bit of which byte the coil M status information is depends on the starting address of M and the quantity of the coils to be read. The address of M is octal. If the returned coil quantity is not a multiple of eight, the remaining bits in the final data byte will be padded with zeros (toward the high order end of the byte). 

Here is an example of reading alarm list coil M1-M8 status (M0 is the lowest coil)
a. Make the alarm list displayed as the following:

b. Use function key to set coil M1.M2.M3.M8 ON and others OFF.
[image: image216.png]Alarm Setting

~Data Setting
PLC Address Type  Address

| o I = )

Index cal Alarm description
0 ML

[

M3

4

s

6

M7

e

Add Insert Delete

ok | cancel




    [image: image217.png]MEHIR
ML M2 M3 M4 M5 M6 M7MS8

N X JCRCECIC)

0

504:  PCYTE|: 55 55 01 48 00 00 00 00 00 00 01 08 00 00 00 00 FC
505: PCAIE: 55 55 FF 01 48 00 00 00 00 00 00 01 02 OE 01 04




Description: The status messages of coil M1-M8: [0E][01]
	Coil No.
	M7
	M6
	M5
	M4
	M3
	M2
	M1
	M0

	Coil status
	0
	0
	0
	0
	1
	1
	1
	0

	data
	0
	E


	Coil No.
	
	
	
	
	
	
	
	M8

	Coil status
	0
	0
	0
	0
	0
	0
	0
	1

	data
	0
	1


When read coil M1-M8 status in controller the data format of query message from SH-300 and response message from controller is shown as following:
	Byte NO.
	Query format (controller receive)
	Example
	Response format (controller send)
	Example

	0
	Framing starting
	55
	Framing starting
	55

	1
	Framing starting
	55
	Framing starting
	55

	2
	Device address
	01
	Response status
	FF

	3
	Function code
	48
	Device address
	01

	4
	Address offset
	00
	Function code
	48

	5
	Reserved byte
	00
	Address offset
	00

	6
	Reserved byte
	00
	Reserved byte
	00

	7
	Address high order bit (Hi)
	00
	Reserved byte
	00

	8
	Address high order bit (Lo)
	00
	Address high order bit (Hi)
	00

	9
	Address Low order bit (Hi)
	00
	Address high order bit (Lo)
	00

	10
	Address Low order bit (Lo)
	01
	Address Low order bit (Hi)
	00

	11
	The quantity of the coil to be read 
	08
	Address Low order bit (Lo)
	01

	12
	Reserved byte
	00
	The byte count occupied by coil status 
	02

	13
	Reserved byte
	00
	Coil status [data 1]
	0E

	14
	Reserved byte
	00
	Coil status [data N]
	01

	15
	Reserved byte
	00
	Verify value
	04

	16
	Verify value
	FC
	
	


4.18 Array FAB Series PLC

SH-300 can communicate with Array FAB series PLC, and the communication port is the programming port of PLC.

SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port

	Default parameter
	9600bps、8bits、1stop、none

	Station No.
	0-254, default value: 0

	Distance (Max.)
	15m

	Communication mode
	RS232

	Cable type
	AF-C232/AF-D232


Explanation: The station number of SH-300 must be the same one as the current address value in FAB communication configuration, or the SH-300 can not communicate with FAB normally.

The description of address types used in SH300 software:
	Object type
	Address type
	Address range
	Read/Write
	Description

	Indicator
	I
	1~12
	Read
	Read input status

	
	Q
	1~8                    
	Read
	Read output status

	
	M
	The number of the corresponding auxiliary relays    in FAB program: (0~127)
	Read
	Read the output status of the function block in FAB program.

	Function key
	Q
	1~8
	Write
	Write the status of empty output port (the output port that is not programmed in FAB program.)

	Dynamic text
	I
	1~12
	Read
	Read input analog value (DC type PLC)

	
	B
	The number of the corresponding function block in SR program: (0~127)
	Read
	Read the parameter value of the function block in FAB program.

	Register
	I
	1~12
	Read
	Read input analog value

	
	B
	The number of the corresponding function block in SR program: (0~127)
	Read
	Read the parameter value of the function block in FAB program.

	
	
	
	Write
	Read the parameter value of the function block in FAB program.

	
	B
	The number of the corresponding function block in SR program
	Read
	Read the parameter value of the function block in FAB program.


Example 1: As the following FAB program shows, SH-300 can display the status of I1~I6, Q1~Q4, and can control the ON/OFF status of Q2, Q3, Q4 through the function key, and can read/write the function blocks B2, B3 as well.

[image: image218.png]13
14
B3
IR E— =
16 L

o1





Example 2: The operation of reading the input/output and the output status of the function block in FAB program.

[image: image219.png]Screen Editor

Property [Lamp]
Posiion

x [# =
v [z =
Style

I Double

Data setting
PLC Address

0 =
Address
1 =

Type

e

Display
Shape

Round ~]

Logic

Positve ~)




Example3: The operation of writing the status of output port (Only the empty port is writable.)

     [image: image220.png]Screen Editor

Praperty [Function key]

Posiion

x [re

vz 3
Style
I™ Double

I™ Reverse

“Touch button
Key

Left -

I™ Hand
I Invisble

I™ password

Action

 set col

 ump to

 Set Register

set Col
PLC Address
o =
Address

1 =

Con
 oFF

@ Feverse)




Example4: Read the analog value and the parameter of the function block in FAB program.

[image: image221.png]



FAB program is shown above. If there is a need to set and display the value of the function block B1 through SH-300, the operation is shown as following graph:

[image: image222.png]oLreEEn Eaior

Property [ Numeric ]

Position Format Data setting
_ | bt PLC Address Max input
x o2 p — 9 < -1 |
v [ =] | Decimal Type I password e
=l 4 p oz Cme | —1

ol Eng. Max

styie Data type P
- oot CregeD || = E
oLble =
o
DEC e Eng. min
I Revese | [ Sioned B £




Explanation: As the SH-300 can not identify second, minute and hour when it is displaying and setting the time of function block, the static text can be used firstly to input the unit that needs to be displayed (e.g. s m h). When SH-300 is setting the time parameter, the fixed format is used: digits: 4, decimal digits: 2, in order to keep the same format as it displayed in FAB program. And when it is setting the analog parameter, the fixed format is used: digits: 3, decimal digits: 1.
4.19 Array SR Series PLC
SH-300 can communicate with Array SR series PLC, and the communication port is the programming port of PLC.

SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port

	Default parameter
	38400bps、8bits、1stop、none

	Distance (Max.)
	15m

	Communication mode
	RS232

	Cable type
	SR-CP


The description of address types used in SH300 software:
	Object type
	Address type
	Address range
	Read/Write
	Description

	Indicator
	I
	IA0~IA7 0.0~0.7

IB0~IB7 1.0~1.7

IC0~IC7 2.0~2.7

ID0~ID7 3.0~3.7

etc.
	Read
	Read the input status.

	
	Q
	QA0~QA7 0.0~0.7

QB0~QB7 1.0~1.7

QC0~QC7 2.0~2.7

QD0~QD7 3.0~3.7

etc.
	Read
	Read the output status.

	
	M
	The number of the corresponding auxiliary relays    in SR program: (0~127)
	Read
	Read the output status of the function block in SR program.

	Register


	ON Delay TOND
	The number of the corresponding function block in SR program: (0~127)
	Read/Write
	 Select “Property Parameter” to set the time for function block.



	
	OFF Delay TOFD
	The number of the corresponding function block in SR program: (0~127)
	Read/Write
	Select “Property Parameter” to set the time for function block.

	
	Single pulse generator PONS


	The number of the corresponding function block in SR program: (0~127)
	Read/Write
	Select “Property Parameter” to set the time for function block.

	
	Clock pulse generator BLNK
	The number of the corresponding function block in SR program: (0~127)
	Read/Write
	Select “Property Parameter” to set the time for function block.

	
	Holding-ON-delay relay MTOD
	The number of the corresponding function block in SR program: (0~127)
	Read/Write
	Select “Property Parameter” to set the time for function block.

	
	UP/DOWN Counter

UDCT
	The number of the corresponding function block in SR program: (0~127)
	Read/Write
	Select “Property Parameter” to set count value for function block.

	
	analog comparator

CMPR
	The number of the corresponding function block in SR program: (0~127)
	Read/Write
	Select “Property Parameter” to set comparison value for function block.

	
	Input analog IN
	0~7
	Read
	Read analog input value

	Garph bar
	ON Delay TOND
	The number of the corresponding function block in SR program: (0~127)
	Read(*2)
	Display the current value of function block.



	
	OFF Delay TOFD
	The number of the corresponding function block in SR program: (0~127)
	Read(*2)
	Display the current value of function block.



	
	Single pulse generator PONS


	The number of the corresponding function block in SR program: (0~127)
	Read(*2)
	Display the current value of function block.



	
	Clock pulse generator BLNK
	The number of the corresponding function block in SR program: (0~127)
	Read(*2)
	Display the current value of function block.



	
	Holding-ON-delay relay MTOD
	The number of the corresponding function block in SR program: (0~127)
	Read(*2)
	Display the current value of function block.



	
	UP/DOWN Counter

UDCT
	The number of the corresponding function block in SR program: (0~127)
	Read(*2)
	Display the current value of function block.



	
	analog comparator

CMPR
	The number of the corresponding function block in SR program: (0~127)
	Read(*2)
	Display the current value of function block.



	
	Input analog IN
	0~7
	Read(*2)
	Dsplay analog input value

	Dynamic text
	UP/DOWN Counter UDCT
	The number of the corresponding function block in SR program: (0~127)
	Read
	Display the dynamic text corresponding to count value.


Note: *1  The text panel displays the time in the format of hour: minute: second-millisecond. If the displayed time exceeds 1 hour, the millisecond will not be displayed.
*2  when the current value of  TOND TOFD PONS  BLNK MTOD function block is displayed by graph bar ,the min and max limit of register = the current value *100

    when the analog input value is displayed by graph bar ,the min and max limit of register = the analog  value *10

4.20 Array TC-Pro Series Digital Timer/Counter/Tachometer
SH-300 can communicate with Array TC-Pro Series digital timer/counter/tachometer through communication port. 

SH-300 software configuration:
	Item
	Content

	SH-300 COM port
	9 pin COM port

	PLC COM port
	Programming port

	Default parameter
	9600bps、7bits、1stop、Even

	Station No.
	0-254, default value: 0

	Distance (Max.)
	15m

	Communication type
	RS232

	Cable type
	CAB-090A232


The description of address types used in SH300 software:
	Object type
	Address type
	Address range
	Read/Write
	Description

	Indicator
	M
	Refer to address list for details
	Read
	Read reset signal and output status of timer/counter/tachometer

	Register


	D
	Refer to address list for details


	Read/Write
	Read and write the register value of timer/counter/tachometer

	Dynamic text
	D
	Refer to address list for details


	Read
	Read the register value of timer/counter/tachometer

	Bar graph/ Trend graph
	D
	Refer to address list for details  
	Read
	Read the register value of timer/counter/tachometer


Note: TC-Pro Series digital timer/counter/tachometer use Hex addresses. the register value is displayed in BCD.

Appendix : Note item

· All basic default function keys except ALM, SET, ESC, ENT, UP, DOWN key can be redefined . If the default function conflict with the defined function, the basic function will be out of action.

· Setting register, press CLR key to enter desired digits. When only a single digit need to
Change, move the cursor to the digit with the direction key and then input the number your need directly. If you want to input A-F in the Hex system, input 0 or 9 and press up/down key .
· If the actual digits of the register exceeds the maximum digits of the setting value the last digit entered is overwritten. So user must set the likely Max. value by the register type when programming.

· When jumping window of screen protection, pressing any key will be invalid and only returned to the original window.

· If the lower limit value of register, bar graph and trend line exceeds its upper limit value  the program won’t be downloaded and you will receive an incorrect report. Please check  it before downloading the program
· When set a new value of register use CLR key to delete the current set value and press the digital key to improve input speed.

· Under the precondition of reliable communication we should make the most of a higher baud rate. Higher baud rate can greatly improve the window refresh rate and decrease the response time for controlling button.
《Memo》





—————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————








Download the Project into Sh-300





Run SH300











Save the Project





Default 


Reference Bar





Display Message Bar





Note Bar





Display Message bar





Modification Message


bar











Modify the coordinate position





Property section





Status bar





Window Description





Edit section





Tool bar





Distribution bar





Menu





《Memo》





———————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————


—————————————————————————————


———————————————————————————————————————————————————————————————————————————————————————





DC24V





COM Port





Contrast Potentiometer





0-9 digital key


+/- sign


CLR Deletion





4.3’’ STN LCD Display





ESC-ESC key


SET-Set key


ENT-enter key


ALM-alarm key





Down key





Right key





Up key





Left key





Modify the text





�





Edit the Screen





《Memo》





—————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————








Create or Open a Project





b. Connect SH-300 with PC, download the 


screen into SH-300.


c. click“�”enter into simulation mode


write 2A6B8C9D hex into two registers 58.59





b. Connect SH-300 with PC, download the screen into SH-300


c. Click“�”to enter into simulation mode. 


Display the set value of Register35 36.





The picture for 6 pin Female plug





Setup SH300





�





The picture for 8 pin Round shape 


Female plug





c. Connect SH-300 with PC


d. Click“�”enter into simulation mode











The picture for 8 pin Round shape 


Female plug





The picture for 8 pin Round shape 


Female plug





�





The picture for 6 pin RJ126 Female plug














The picture for ５pin Round shape Female plug











The picture for 8 pin Round shape 


Female plug








《Memo》





—————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————————











Page 61 of 97
Page 54 of 97
Page 9 of 97

